## TRAM Instructions
Tiered Risk Assessment Management (TRAM) Proposal Template Instructions
The TRAM Proposal template was developed to help applicants utilizing rainwater harvesting in their Stormwater Management Plan (SWMP) to meet the requirements of Appendix M Tiered Risk Assessment Management: Water Quality End Use Standards of the DC Stormwater Management Guidelines and is customizable to the applicant’s specific project. The TRAM Proposal template is an editable document file, so the applicant can easily add tables, graphs, sampling results, and additional text. The applicant can also remove any sections that are not relevant to the project. Prior to using the template, read Appendix M Tiered Risk Assessment Management Water Quality End Use Standards to understand the application process for rainwater harvesting systems. The process requires the use of the TRAM approach to assess microbial and chemical contaminants of concern in the stormwater catchment area and the public health threat posed by the contaminants. The completed TRAM Proposal should be incorporated into the SWMP submittal to DDOE.
GENERAL
General | Incorporate the TRAM Report by reference into the plan set by adding a note referring to the TRAM Report, acceptance date, and report author in the stormwater harvesting system specifications.
STEP 1: SITE INVESTIGATION
1.1 Site Location Map | Provide a site location map showing all properties in the proposed stormwater catchment system. Label each property and provide the total acreage of the stormwater catchment.
1.2.1 Zoning Classification Table | Use the table to provide zoning classification of all properties contributing to the stormwater catchment. See the following website more the Washington DC Zoning Map: http://zmap.dcoz.dc.gov/.
1.2.2 Potential Contaminants In Industrial Zones | For all sites zoned as industrial where the proposed catchment area contains surfaces other than the proposed roof area, determine if chemical or microbial contamination is present and provide findings in the table. In the Location column, identify the general location where the potential contaminant was used, stored, or released on the property. Remove section if not applicable.
1.3 Historic Site Conditions | Provide a narrative of how the property has historically been used. Focus particularly on the following land uses: ▪ Industrial land uses ▪ Runoff from major roads and freeways with high traffic volumes ▪ Residential areas that experience frequent sewer overflows ▪ Stormwater hotspot concerns (see Stormwater Management Guidebook Appendix P Stormwater Hotspots for a list of hotspot operations)
1.4.1 Existing Conditions Description | Provide an overall description of the site property and the surrounding areas.
1.4.2 Planned Future Uses | Provide planned future uses of the site.
1.4.3 Environmental Investigations | Provide a description of any portion of the site regulated by the Resource Conservation and Recovery Act (RCRA), Superfund Program, or any other environmental investigation. Include note if not applicable.
1.4.4 Environmental Enforcement Actions | Insert the current status of ongoing or unresolved Consent Orders, Compliance Agreements, Notice of Violations (NOV), or other activities. Include note if not applicable.
1.4.5 Existing Conditions Schematic | Insert an existing conditions schematic with the location of sewer manholes, any obvious chemical spills, and above and underground storage tanks. If not applicable, remove section.
1.4.6 Roof Catchment Area Characteristics | Check all that apply to the roof catchment area and provide any supplemental information. Unless the items checked are addressed with special treatment or diversion, the rooftop stormwater cannot be collected. If not applicable, check "My site does not contain any of these elements."
1.5.1 Stormwater Collection and Storage | In the table, identify the catchment area, list how stormwater will be collected (roof water, parking lots, etc.) in the catchment area and how stormwater will be stored (aboveground cistern, belowground storage tank, etc.).
1.5.2 Stormwater End Use and Exposure Routes | Create a table of potential exposures for each end use (municipal irrigation, spray fountain, pool, etc.). See Table M. 4 Chemicals of Interest for Baseline Investigation (Appendix M Tiered Risk Assessment Management (TRAM)- Step 1, page M-11). The table should include the following: ▪ Exposed Individuals- List of all types of individuals who could potentially be exposed to stormwater under the intended use (i.e. landscapers, maintenance workers, children, joggers, etc.) ▪ Age Group- Age groups for all types of exposed individuals (i.e. children, adults, elderly) ▪ Sensitive Population- Sensitive populations that may be exposed (children, infirm, invalid, etc.) ▪ Estimated Exposure Time- Estimated time (i.e. hours, days, years) each type of individual could be exposed to stormwater under its intended use ▪ Activities- Activities the exposed individuals will engage in on site (recreational, sports, gardening, etc.) ▪ Type and Routes of Exposure- Type and routes of exposures for all exposed individuals (ingestion of sprays during irrigation, ingestion during car wash, ingestion of fruits and vegetables irrigated with stormwater, etc.) ▪ Exposure from Unintended Stormwater Use- Potential exposures associated with unintended stormwater uses (i.e. system malfunction, cross plumbing, etc.)
STEP 2: LIKELIHOOD OF EXPOSURE
2.1 Likelihood of Exposure | Using the classifications listed in Table M.1 Likelihood of Exposure to Occur (Appendix M Tiered Risk Assessment Management (TRAM), page M-4), determine if the exposure is unlikely, possible, or likely to occur and fill in the table. Refer to Table M.6 Exposure Assumptions Based on Stormwater Use and Exposure Conditions (Appendix M Tiered Risk Assessment Management (TRAM), page M-13) for a better understanding of ingestion risks and time of exposure. In the comment column, explain why the exposure classification was selected.
Decision Point 1: Are Exposures Likely? | If the information provided in Steps 1 and 2 supports a determination that exposures are “unlikely,” no further study or analysis is required. If the information provided supports a determination that exposure is “possible” or “likely,” an evaluation of maximum risk based on the concentration of contaminants is required. Continue to Step 3 and provide additional information on activities where human exposures are “possible” or “likely”.
STEP 3: CONCENTRATION OF CONTAMINANTS IN STORMWATER
3.1.1 Contaminant List | For systems harvesting stormwater from an existing catchment or rooftop, provide a list of all chemicals to be sampled. Include all chemicals identified in Step 1. New building roof projects can remove Steps 3.1.1-3.1.3 and move to Step 3.1.4.
3.1.2 Sampling Location Map | Include a sampling location map with the number of samples collected at each location.
3.1.3 Sampling Plan | Provide a sampling method used to determine the concentration of contaminants in stormwater. Explain how the sampling method: ▪ Represents the conditions that will occur during a major storm event ▪ Takes into account roof, soil, and solid surface contributions to the stormwater catchment system ▪For example, if collected stormwater will be stored in a cistern shield from light for several days before it is used, the samples sent for laboratory analysis must be stored under the same conditions.
3.2.1 New Building Roof Materials | Identify the proposed roofing materials for the new building. Systems harvesting stormwater from an existing catchment or rooftop can remove Steps 3.2.1-3.2.3 and move to Step 4.
3.2.2 Contaminant List | In the table, list any potential contaminants of concern, such as copper, zinc, nitrate, and phosphorus, associated with the roofing materials. All new building roof projects should include E. coli as a potential contaminant.
3.2.3 Estimated Concentrations for New Roof | Use published literature to estimate proposed roof concentration for the contaminants of concern. See the following publications for estimated contaminant concentrations (check concentration units to make sure they match the RSLs): Aluminum, Shingle, Galvanized Metal, and Tar Roofs ▪ DeBusk, Kathy, et al. "Water Quality of Rooftop Runoff: Implications for Residential Water Harvesting Systems." Urban Waterways North Carolina Cooperative Extension http://www.bae.ncsu.edu/stormwater/PublicationFiles/RooftopRunoff2009.pdf Shingle Roofs ▪ Haberland, M., et al. "An Investigation of the Water Quality of Rainwater Harvesting Systems." Journal of the NACAA, May 2013, Volume 6 Issue 1 http://www.nacaa.com/journal/index.php?jid=205 Shingle, Galvanized Metal, and Wood Roofs ▪ Clark, Shirley, et al. "Runoff Quality from Roofing Materials During Early Life." Penn State Harrisburg http://www.personal.psu.edu/faculty/s/e/sec16/index_files/clark%20weftec%20roof%20comparison.pdf
STEP 4: STORMWATER CONCENTRATIONS COMPARISONS WITH RISK BASED LEVELS
4.1 Exposure Conditions and Intensity | Using the routes of exposure and estimated exposure times listed in Step 1, identify the exposure conditions in Table M.6 Exposure Assumptions Based on Stormwater Use and Exposure Conditions (Appendix M Tiered Risk Assessment Management (TRAM), page M-13) that most closely match site-specific conditions. Use Table M.7 Categorizing Exposures Based On Stormwater Use: Severe, High, Medium, and Low (Appendix M Tiered Risk Assessment Management (TRAM), page M-13) to identify the exposure intensity for each stormwater use that best represents the site conditions. Fill out the first table for each end use and route of exposure. In addition to the planned stormwater use, consider the inadvertent or unauthorized use of stormwater and fill out the second table. Unintended stormwater uses may result in higher-than-intended exposure to humans and the receiving environment.
4.2 Risk- Based Screening | Using the DDOE derived RSLs listed in Table M.8 Risk-based Chemical Concentrations for Sites Categorized as Severe, High, Medium, and Low Exposures (Appendix M Tiered Risk Assessment Management (TRAM), page M-16) fill out the first table to compare the sample or estimated concentrations to the RSL. Convert all concentrations to appropriate units for comparison. Using the DDOE derived RSLs listed in Table M.9 Risk-based Microbial Levels for Sites Categorized as Severe, High, Medium, and Low Exposures (Appendix M Tiered Risk Assessment Management (TRAM), page M-18), fill out the second table to compare the sample or estimated E. coli concentrations to the RSL. If the sample E. coli concentration exceeds the RSL, use the DDOE derived RSLs listed in Table M.9 Risk-based Microbial Levels for Sites Categorized as Severe, High, Medium, and Low Exposures (Appendix M Tiered Risk Assessment Management (TRAM), page M-18) to compare the C. parvum sample concentrations to the RSL.
Decision Point 2: Is Maximum Risk for Untreated Stormwater Acceptable? | Determine if any contaminants failed the risk-based screening. If no contaminants failed the risk-based screening, stormwater does not pose a threat to human health and no further action is necessary. If one or more contaminants failed the risk-based screening, continue to Step 5 to take actions to lower the risks to an acceptable level. If the contaminants exceed the RSLs by less than one or two orders of magnitude, DDOE can exercise its discretion about whether a treatment system is necessary by looking at the availability of treatment systems, severity of the toxic effect, probability of exposures, and whether measures can be implemented to prevent exposures.
STEP 5: TREATMENT TECHNOLOGY SELECTION
5.1 Treatment Technology | Select the appropriate treatment technology to reduce contaminants to acceptable risk levels. The type of treatment selected must target the specific chemical and/or microbial contaminants that failed risk-based screening in Step 4. Provide a full description of the treatment system, specifications, system operating efficiency, construction sequencing, maintenance tasks, and inspection requirements.
STEP 6: COMMISSIONING PROGRAM
6.1 Commissioning Program | Develop a verification sampling plan to validate the treatment system is operating as designed. More extensive sampling is required for projects where a greater number of individuals are exposed to chemicals that are considered more toxic. The commissioning program should take into account both peak and average rainfalls and identify the point of compliance as the stormwater catchment.
STEP 7: TREATED STORMWATER CONCENTRATIONS COMPARISONS WITH RISK BASED LEVELS
7.1 Treated Stormwater Concentrations | In the table, compare the maximum (untreated stormwater) and residual (treated stormwater) risk to determine the log reduction necessary to achieve acceptable risk levels. Sample concentrations should be less than the RSLs.
Decision Point 3: Is the Residual Risk for Treated Stormwater Acceptable? | Determine if the stormwater treatment technology effectively reduced contaminant levels to acceptable concentrations. If the treatments system reduced contaminant levels to acceptable concentrations, provide verification samples results and conclusions indicating the treatment system is performing as designed. If the treatments system failed to reduce contaminant levels to acceptable concentrations, provide an explanation for the failure and identify modifications to the selected treatment system or an alternate technology that will achieve the desired concentration. If the proposed and DDOE approved stormwater treatment technology fails to adequately reduce contaminants at commissioning, the treatment system requires redesign and additional DDOE review. Repeat Steps 5 through 7.
STEP 8: POST-CONSTRUCTION MONITORING PROGRAM
8.1 Post-Construction Monitoring Program | Submit a post-construction monitoring program to confirm continued compliance with the required end use water standards. The post-monitoring program must also be included in the Declaration of Covenant as part of the rainwater harvesting systems long term maintenance obligations. The monitoring plan should assess and address: ▪ Annual verification of stormwater treatment technology performance by comparing sample concentrations to the RSLs ▪ Performance evaluation after significant maintenance or modifications to the treatment system If any changes occur in the receiving environment or exposed populations, you must notify DDOE and complete an updated TRAM report.

## Step 1
1.2.1 Zoning Classification Table
PROPERTY | ADDRESS | ZONING CLASSIFICATION
1.2.2 Potential Contaminants in Industrial Zones
INDUSTRIAL PROPERTY | POTENTIAL CONTAMINANT |  | LOCATION
| CHEMICAL | MICROBIAL
1.5.1 Stormwater Collection and Storage Table
STORMWATER CATCHMENT AREA | STORMWATER COLLECTION SYSTEM | STORMWATER STORAGE SYSTEM
1.5.1 Stormwater End Use Table
POTENTIAL EXPOSURES
EXPOSED INDIVIDUALS | AGE GROUP | SENSITIVE POPULATION | ESTIMATED EXPOSURE TIME | ACTIVITIES | TYPE AND ROUTE OF EXPOSURE | EXPOSURE FROM UNINTENDED STORMWATER USE

## Step 2
2.1 Likelihood of Exposure Table
STORMWATER END USE | EXPOSED INDIVIDUALS | ACTIVITIES | LIKELIHOOD OF EXPOSURE | COMMENTS

## Step 3
3.1.1 Contaminant List
INORGANIC METALS | ORGANIC COMPOUNDS | PESTICIDES | PATHOGENIC MICROBES
3.1.2 Sampling Location Map Table
SAMPLING LOCATION | # OF SAMPLES TAKEN

## Step 4
4.1 Exposure Conditions and Intensity Tables
STORMWATER END USE | ROUTE OF EXPOSURE | EXPOSURE ASSUMPTIONS |  | EXPOSURE INTENSITY (SEVERE, HIGH, MED, LOW)
|  | VOLUME INGESTED (mL) | DAYS (PER YEAR)
UNINTENDED/ UNAUTHORIZED STORMWATER USE | ROUTE OF EXPOSURE | EXPOSURE ASSUMPTIONS |  | EXPOSURE INTENSITY (SEVERE, HIGH, MED, LOW)
|  | VOLUME INGESTED (mL) | DAYS (PER YEAR)
4.2A Risk Based Screening Chemical Table
CHEMICAL | RSL CONCENTRATION (µg/L) | SAMPLE/ ANTICIPATED CONCENTRATION (µg/L) | DOES SAMPLE CONCENTRATION EXCEED RSL?
4.2B Risk Based Screening Escherichia Coli Table
E. COLI | RSL CONCENTRATION (CFU/mL) | SAMPLE/ ANTICIPATED CONCENTRATION (CFU/mL) | DOES SAMPLE CONCENTRATION EXCEED RSL?
4.2C Risk Based Screening C. Parvum Table
C. PARVUM | RSL CONCENTRATION (CFU/mL) | SAMPLE CONCENTRATION (CFU/mL) | DOES SAMPLE CONCENTRATION EXCEED RSL?

## Step 7
7.1 Comparison of Treated Stormwater to RSL Table
CHEMICAL | RSL CONCENTRATION (µg/L) | TREATED SAMPLE CONCENTRATION (µg/L) | DOES SAMPLE CONCENTRATION EXCEED RSL?