January 7, 2014

Ms. Michele Blazek, Assistant Secretary

New Cingular Wireless PCS, LLC, dba AT&T Mobility

2600 Camino Ramon Rm. 3E450Z

San Ramon, CA 94583

RE:	Batch Permits to Construct and Operate Emergency Diesel Generator Sets

Dear Ms. Blazek:

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit from the District Department of the Environment (the Department) shall be obtained before any person can construct and operate a stationary source in the District of Columbia. The applications of New Cingular Wireless PCS, LLC, dba AT&T Mobility (the Permittee) to construct and operate the identical diesel-fired Generac emergency generator sets listed in Table 1, located in Washington, DC, have been reviewed.

Based on the submitted plans and specifications as detailed in the applications with cover letter dated July 30, 2013, and received on August 2, 2013, the applications are hereby approved, and the construction and operation of the emergency generator sets are permitted, subject to the following conditions:

I.	General Requirements:

- The emergency generator sets shall be operated in accordance with the air pollution control requirements of 20 DCMR.

b.	This set of permits will expire on January 6, 2019 [20 DCMR 200.4].  If continued operation after this date is desired, the owner or operator shall submit applications for renewal by October 6, 2018.

c.	Construction or operation of equipment under the authority of this set of permits shall be considered acceptance of its terms and conditions.

- The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1.	Enter upon the Permittee’s premises where a source or emission unit is located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this set of permits; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this set of permits or any applicable requirement.

- The original or a copy of this set of permits shall be kept on the premises or location of each emergency generator and produced upon request.

- Failure to comply with the provisions of this set of permits may be grounds for suspension or revocation. [20 DCMR 202.2]

Table 1. – Permitted Emergency Generator Sets

| Equipment Location | Address | Generator Standby Rating (Engine Size) | Model Numbers (Engine/ Generator) | Permit No. |
| --- | --- | --- | --- | --- |
| 700 Constitution Ave. SE, Washington, DC | 700 Constitution Ave. SE, Washington, DC 20004 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6761 |
| 1730 17th St. NW, Washington, DC | 1730 17th St. NW, Washington, DC 20001 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6762 |
| 2001 1st Street SW, Washington, DC | 20011st Street SW, Washington, DC 20593 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6763 |
| 2440 Virginia Ave. NW, Washington, DC | 2440 Virginia Ave. NW, Washington, DC 20037 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6764 |
| 1420 Columbia Rd. NW, Washington, DC | 1420 Columbia Rd. NW, Washington, DC 20009 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6765 |
| 5505 5th Street NW, Washington, DC | 5505 5th Street NW, Washington, DC 20011 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6766 |
| 1130 Connecticut Ave. NW, Washington, DC | 1130 Connecticut Ave. NW, Washington, DC 20036 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6767 |
| 1275 Pennsylvania Ave. NW, Washington, DC | 1275 Pennsylvania Ave. NW, Washington, DC 20004 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6768 |
| 901 F Street NW, Washington, DC | 901 F Street NW, Washington, DC 20004 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6769 |
| 1310 Wisconsin Ave. NW, Washington, DC | 1310 Wisconsin Ave. NW, Washington, DC 20007 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6770 |
| 2700 Connecticut Ave. NW, Washington, DC | 2700 Connecticut Ave. NW, Washington, DC 20008 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6771 |
| 1601 Connecticut Ave. NW, Washington, DC | 1601 Connecticut Ave. NW, Washington, DC 20009 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6772 |
| 1625 Massachusetts Ave. NW, Washington, DC | 1625 Massachusetts Ave. NW, Washington, DC 20036 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6773 |
| 930 M Street NW, Washington, DC | 930 M Street NW, Washington, DC 20001 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6774 |
| 611 Edgewood Terrace NE, Washington, DC | 611 Edgewood Terrace NE, Washington, DC 20017 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6775 |
| 2540 Massachusetts Ave. NW, Washington, DC | 2540 Massachusetts Ave. NW, Washington, DC 20008 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6776 |
| 4000 Brandywine St. NW, Washington, DC | 4000 Brandywine St. NW, Washington, DC 20016 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6777 |
| 1900 Massachusetts Ave. SE, Washington, DC | 1900 Massachusetts Ave. SE, Washington, DC 20003 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6778 |
| 51 N Street NE, Washington, DC | 51 N Street NE, Washington, DC 20002 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6779 |
| 2480 16th Street NW, SE, Washington, DC | 2480 16th Street NW, Washington, DC 20009 | 50 kW (93 bhp/69.4 kW) | Iveco/FTP SD050/ | 6780 |

II.	Emission Limitations:

- Emissions shall not exceed those found in the following table, as measured according to the procedures set forth in 40 CFR 89, Subpart E. [40 CFR 60.4205(b), 40 CFR 60.4202(a)(2) and 40 CFR 89.112(a)]

| Emission Standards |
| --- |
| Pollutant | g/kW-hr |
| NMHC+NOx | 4.7 |
| CO | 5.0 |
| PM | 0.4 |

  - b.	Visible emissions shall not be emitted into the outdoor atmosphere from each generator, except that discharges not exceeding forty percent (40%) opacity (unaveraged) shall be permitted for two (2) minutes in any sixty (60) minute period and for an aggregate of twelve (12) minutes in any twenty-four hour (24 hr.) period during start-up, cleaning, adjustment of combustion controls, or malfunction of the equipment [20 DCMR 606.1]

c.	An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1]

III.	Operational Limitations:

  - a.	Each emergency generator shall not be operated in excess of 500 hours in any given 12 month period.  If operation beyond 500 hours is desired, the owner or operator shall submit an application to amend this permit to comply with the conditions of 20 DCMR 805 and shall obtain the Department’s approval of such application prior to initiating such operation.

- With the exceptions specified in Condition III(c), each emergency generator shall be operated only during emergencies as follows:

1.   An electrical power outage due to: a failure of the electrical grid; on-site disaster; local equipment failure; or public service emergencies such as flood, fire, natural disaster, or severe weather conditions (e.g. hurricane, tornado, blizzard, etc.);

2.	For a period up to 15 hours per calendar year when there is a substantial deviation of voltage or frequency from the electrical provider to the premises of 5 percent or more below standard voltage or frequency such that the equipment being supported cannot be safely or effectively operated; or

3.	When a sudden, unexpected event occurs that, if not immediately attended to, presents a safety or public health hazard, is necessary to protect equipment from damage, or is necessary to avoid imposing an unreasonable financial burden.  An emergency includes operations necessitated by non-routine failures of equipment, but it does not include voluntary demand reductions covered by Condition III(f).

- Each emergency generator may be operated for the purpose of maintenance checks and readiness testing for a period not to exceed one hundred (100) hours per year as specified in Condition III(c)(1) and (2) below.  Any such operation shall be considered as part of the 500 hours allowed under Condition III (a) above. [40 CFR 60.4211(f)]

1.	Each emergency generator may be operated for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. [40 CFR 60.4211(f)(2)(i) and DCMR 201]; and

2.	Each emergency generator may be operated for up fifty (50) hours per calendar year in non-emergency situations.  Any such operations shall be counted as part of the 100 hours per calendar year for maintenance and testing as provided in Condition III(c).  These 50 hours of non-emergency operations per calendar year cannot be used for peak shaving, or as part of any program to supply power to generate income for the facility as part of a financial arrangement with another entity.  All operations prohibited under Condition III(f) are also prohibited under this condition. [40 CFR 60.4211(f)(3) and 20 DCMR 201]

- Each emergency generator shall fire only diesel fuel which contains a maximum sulfur content of 15 ppm (0.0015 percent by weight) and either a cetane index of 40 or a maximum aromatic content of 35 volume percent. [40 CFR 60.4207(b)]

e.	The emergency generators shall be operated and maintained in accordance with the recommendations of the equipment manufacturer.

f.	The emergency generators shall not be operated in conjunction with a voluntary demand-reduction program or any other interruptible power supply arrangement with a utility, other market participant, or system operator.

g.	At all times, including periods of startup, shutdown, and malfunction, the owner shall, to the extent practicable, maintain and operate the units in a manner consistent with good air pollution control practice for minimizing emissions.  Determination of whether acceptable operating procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source.

IV.	Monitoring and Testing Requirements:

a.	The owner or operator shall monitor the date, time, duration, and reason for the emergency generator startup.

b.	In order to ensure compliance with Condition III(a), the owner or operator shall monitor the total hours of operation each month with the use of a properly functioning, non-resettable hour metering device.

c.	The owner or operator shall test fuel oil as necessary to show compliance with Conditions III(d) and V(c) in accordance with appropriate ASTM methods. [20 DCMR 502.6]

d.	The owner or operator shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested.  [20 DCMR 502.1]

V.	Record Keeping Requirements:

- The following information shall be recorded, initialed, and maintained in a log at the facility for a period not less than three (3) years [20 DCMR 500.8]:

1.	The date, time, duration, and reason for each start-up of the emergency generator, including the following specific information:

i.	If the unit is operated due to a deviation in voltage from the utility pursuant to Condition III(b)(2) this shall be specifically noted;

ii.	If the unit is operated in non-emergency situations pursuant to Condition III(c), the specific purpose for each operation period must be recorded; and

iii.	If the unit is operated for emergency purposes, what classified the operation as emergency.

2.	The total hours of operation for each month and the cumulative 12-month rolling period shall be calculated and recorded within 15 days of the end of each calendar month;

3.	The total hours of operation due to a deviation in voltage from the utility pursuant to Condition III(b)(2) each calendar year;

4.	Records of the maintenance performed on the unit; and

5.	Records of the results of any visible emissions monitoring performed.

6.	Records of the occurrence and duration of each malfunction of operation; and

7.	Records of the actions taken during periods of malfunction to minimize emissions, including corrective actions to restore malfunction process and air pollution control and monitoring equipment to its normal or usual manner of operation.

b.	The owner or operator shall maintain a copy of the emergency generator manufacturer’s maintenance and operating recommendations at the facility and/or location of each emergency generator.

c.	For each delivery of diesel fuel, the owner or operator shall maintain one of the following:

1.	A fuel delivery receipt containing the date, fuel type, and amount of the delivery and certification from the fuel supplier that the fuel delivered was tested in accordance with an appropriate ASTM method (specified in the certification) and met the requirements of Condition III(d); or

2.	A fuel delivery receipt and documentation of sampling and analysis containing the following information:

A.	The fuel oil type;

B.	The concentration or weight percent of sulfur in the fuel;

C.	The date and time the sample was taken;

D.	The name, address, and telephone number of the laboratory that analyzed the sample; and

E.	The test method used to determine the sulfur content.

d.	The owner or operator shall maintain a copy of the EPA Certificate of Conformity at the facility at all times.

If you have any questions, please call me at (202) 535-1747 or John Nwoke at (202) 724-7778.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:JCN

cc:	Barbara Walden, Manager, Environment, Health and Safety, New Cingular Wireless PCS, LLC dba AT&T Mobility, 2600 Camino Ramon, Room 3E450Y, San Ramon, CA 94583