April 30, 2013

Mr. James Schrote, 				Permittee: The George Washington University

Executive Director, Facilities

The George Washington University

Operations Division

2025 F Street, NW, Suite 215

Washington, DC 20052

RE:	Permits to Operate Ivory Tower Dual Fuel-Fired Hot Water Boilers

Dear Mr. Schrote:

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit from the District Department of the Environment (the Department) shall be obtained before any person can construct and operate a stationary source in the District of Columbia. The Permittee’s applications to operate the listed two Smith Cast Iron dual fuel-fired (natural gas and No. 2 fuel oil) hot water boilers, located in Washington, DC, have been reviewed:

| Equipment Location | Address | Equipment Size (MMBtu/hr Heat Input) | Serial Number | Permit No. |
| --- | --- | --- | --- | --- |
| Ivory Tower | 616 23rd Street NW Washington, DC | 9.73 | 60308933 | 6688 |
| Ivory Tower | 616 23rd Street NW Washington, DC | 9.73 | 60308934 | 6689 |

Based on the submitted plans and specifications as detailed in the applications received on November 1, 2012, the applications are hereby approved, and the operation of the hot water boilers is permitted, subject to the following conditions:

I.	General Requirements:

  - The approval is issued pursuant to the applicable air pollution control requirements of 20 DCMR for the operation of the heating boilers.

b.	This set of permits will expire on April 29, 2018.  If continued operation after this date is desired, the owner or operator shall submit applications for renewal by January 29, 2018. [20 DCMR 200.4]

c.	Operation of equipment under the authority of this set of permits shall be considered acceptance of its terms and conditions.

- The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1.	Enter upon the Permittee’s premises where a source or emission unit is located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

- This set of permits shall be kept on the premises and produced upon request.

- Failure to comply with the provisions of this permit document may be grounds for suspension or revocation. [20 DCMR 202.2]

g.	Emergency situations shall be handled in accordance with the provisions of 20 DCMR 302.7 (a) through (c).

h.	If not already completed by the date of this permit, within twelve (12) months of issuance of this permit to operate, the Permittee shall submit a complete application to modify the facility’s Title V operating permit to include the requirements of this set of permits [20 DCMR 301.1(a)(3)].  This application is due by April 29, 2014.

II.	Emission Limitations:

  - Each of the two (2) identical 9.73 million BTU per hour (Natural Gas) Smith dual fuel (No. 2 fuel oil/natural gas) fired boilers identified as IVT-B1 and IVT-B2, shall not emit pollutants in excess of those specified in the following table [20 DCMR 201]:

| Boiler Emission Limits |
| --- |
| Pollutant | Short-Term Limit (Natural Gas) (lb/hr) | Short-Term Limit (#2 Fuel Oil) (lb/hr) | Annual Emissions Limit (ton/yr) |
| Carbon Monoxide (CO) | 0.80 | 0.35 | 3.51 |
| Oxides of Nitrogen (NOx) | 0.95 | 1.41 | 4.18 |
| Particulate Matter < 10 microns (PM10) | 0.07 | 0.23 | 0.32 |
| Volatile Organic Compounds (VOC) | 0.05 | 0.02 | 0.23 |
| Sulfur Dioxide (SO2) | 0.01 | 2.02 | 0.02 |

  - b.	Particulate matter emissions from boilers IVT-B1and IVT-B2 shall not exceed 0.102 pounds per million BTU on a per boiler basis. [20 DCMR 600.1]

c.	Visible emissions shall not be emitted into the outdoor atmosphere from each boiler; except that no greater than 40% opacity (unaveraged) shall be permitted for two minutes per hour and for an aggregate of twelve minutes per 24-hour period during start-up, cleaning, soot blowing, adjustment of combustion controls, or malfunction.[20 DCMR 606.1]

d.	An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1]

III.	Operational Limitations:

  - a.	The primary fuel for the boilers shall be natural gas with a maximum sulfur content of 2.5 grains per 100 standard cubic feet.  No. 2 fuel oil may be used as a secondary fuel.  [20 DCMR 201]

- The boilers shall be operated at all times in a manner consistent with the manufacturer’s specifications for the equipment. [20 DCMR 201]

- The Permittee shall perform tune-ups on each unit on a biennial basis.  The first tune-up must be performed by March 21, 2014.  Subsequent tune-ups must be conducted no more than 25 months after the previous tune-up. [40 CFR 63.11201(b) and 63.11223(a)]

- In order to demonstrate continuous compliance, each biennial tune-up shall be performed to meet the following criteria: [20 CFR 63.11223(b)]

1.	As applicable, inspect the burner, and clean or replace any components of the burner as necessary (you may delay the burner inspection until the next scheduled unit shutdown, not to exceed36 months from the previous inspection).

2.	Inspect the flame pattern, as applicable, and adjust the burner as necessary to optimize the flame pattern. The adjustment should be consistent with the manufacturer's specifications, if available.

3.	Inspect the system controlling the air-to-fuel ratio, as applicable, and ensure that it is correctly calibrated and functioning properly (you may delay the inspection until the next scheduled unit shutdown, not to exceed 36 months from the previous inspection).

4.	Optimize total emissions of carbon monoxide. This optimization should be consistent with the manufacturer's specifications, if available, and with any nitrogen oxide requirement to which the unit is subject.

5.	Measure the concentrations in the effluent stream of carbon monoxide in parts per million, by volume, and oxygen in volume percent, before and after the adjustments are made (measurements may be either on a dry or wet basis, as long as it is the same basis before and after the adjustments are made). Measurements may be taken using a portable carbon monoxide analyzer.

6.	If the unit is not operating on the required date for a tune-up, the tune-up must be conducted within 30 days of startup.

IV.	Monitoring and Testing Requirements:

a.	If a stack test to determine compliance with Condition II(a), (b), and/or (d) is requested by the Department in accordance with 20 DCMR 502.1, the written report of the results of such a stack test shall be furnished to the District in accordance with the following requirements [20 DCMR 502]

1.	One (1) original and one (1) copy of the test protocol shall be submitted to the following address a minimum of thirty (30) days in advance of the proposed test date.  The test shall be conducted in accordance with Federal and District requirements.

Chief, Compliance and Enforcement Branch

Air Quality Division

1200 First Street NE

5th Floor

Washington, DC 20002

2.	The test protocol shall be approved by the Department prior to initiating any testing.  Upon approval of the test protocol, the Company shall finalize the test date with the assigned inspector in the Permitting and Enforcement Branch.  The Department must have the opportunity to observe the test for the results to be considered for acceptance.

3.	The final results of the testing shall be submitted to the Department within sixty (60) days of the test completion.  One (1) original and one (1) copy of the test report shall be submitted to the address in Condition IV (a)(1) above.

4.	The final report of the results shall include the emissions test report (including raw data from the test) as well as a summary of the test results and a statement of compliance or non-compliance with permit conditions to be considered valid.  The summary of results and statement of compliance or non-compliance shall contain the following information:

A.	A statement that the owner or operator has reviewed the report from the emissions testing firm and agrees with the findings.

B.	Permit number(s) and condition(s) which are the basis for the compliance evaluation.

C.	Summary of results with respect to each permit condition.

D.	Statement of compliance or non-compliance with each permit condition.

5.	The results must demonstrate to the Department’s satisfaction that the emission unit is operating in compliance with the applicable regulations and conditions of this permit; if the final report of the test results shows non-compliance the owner or operator shall propose corrective action(s).  Failure to demonstrate compliance through the test may result in enforcement action.

b.	The owner or operator shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested.  [20 DCMR 502.1]

c.	The owner or operator shall test fuel oil as necessary to show compliance with Condition III (a) in accordance with appropriate ASTM methods. [20 DCMR 502.6]

d.	The Permittee shall monitor the quantity of each fuel used in each boiler each month.

e.	At least once per month, during operation of each boiler, the Permittee shall conduct visual observations of the emissions from each boiler.  If no operations are occurring for a given boiler during a given month, this shall be so noted.  If emissions are visible, the Permittee shall make arrangements for prompt visible emissions testing by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).  Such a test shall consist of a minimum of 30 minutes of opacity observations for the boiler in question and shall be performed while firing the same fuel as was in use when the visible emissions were observed.

f.	Regardless of whether or not emissions are observed pursuant to Condition IV (c) of this permit, the Permittee shall conduct a minimum of one visible emissions test of each boiler each year for each fuel burned that year.  Such a test program shall consist of a minimum of 30 minutes of opacity observations of each boiler firing each fuel and shall be performed by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).

V.	Record Keeping and Reporting Requirements:

The following information shall be maintained at the facility for a period not less than five (5) years [20 DCMR 500.8 and 20 DCMR 302.1(c)(2)(B)]:

a.	The Permittee shall keep records of the results of all emissions testing and sampling required for the boilers pursuant to Conditions IV (a), (b), (c), (e) and (f) of this permit document.

b.	For each delivery of No. 2 fuel oil or diesel fuel, the owner or operator shall maintain one of the following:

1.	A fuel delivery receipt containing the date, fuel type, and amount of the delivery and certification from the fuel supplier that the fuel delivered was tested in accordance with an appropriate ASTM method (specified in the certification) and met the requirements of Condition III(a); or

2.	A fuel delivery receipt and documentation of sampling and analysis containing the following information:

A.	The fuel oil type;

B.	The concentration or weight percent of sulfur in the fuel;

C.	The date and time the sample was taken;

D.	The name, address, and telephone number of the laboratory that analyzed the sample; and

E.	The test method used to determine the sulfur content.

c. 	The Permittee shall maintain records of the amount of each fuel used each month in each boiler.  These data shall be maintained in a rolling twelve month sum format [20 DCMR 500.2]

d.	Maintain onsite and submit, if requested by the EPA Administrator or the Department, a biennial report containing the information in paragraphs V (d)(1) through (3) of this section.

1.	The concentrations of CO in the effluent stream in parts per million, by volume, and oxygen in volume percent, measured at high fire or typical operating load, measured before and after the tune-up of the boiler.

2.	A description of any corrective actions taken as a part of the tune-up of the boiler.

3.	The type and amount of fuel used over the 12 months prior to the tune-up of the boiler.

e.	If not already completed at the time of issuance of this permit, submit an “Initial Notification of Applicability” with regard to the EPA Administrator with respect to the applicability of 40 CFR 63, Subpart JJJJJJ, National Emission Standards for Hazardous Air Pollutants for Industrial, Commercial, and Institutional Boilers Area Sources as required by 40 CFR 63.11225(a)(4).

f.	Submit a biennial compliance report containing the following information with the annual Title V compliance certification required pursuant to the Title V Operating permit for the equipment covered by this permit, upon issuance or by March 1, 2013 (whichever occurs first) and every two years thereafter [40 CFR 63.11225(b)]:

1.	Company name and address;

2.	Statement by a responsible official, with the official's name, title, phone number, e-mail address, and signature, certifying the truth, accuracy and completeness of the notification and a statement of whether the source has complied with all the relevant standards and other requirements of this subpart.  The notification must include the following certification of compliance, and be signed by a responsible official:

“This facilities complies with the requirements in 40 CFR 63.11223 to conduct a biennial or 5-year tune-up, as applicable, of each boiler.”

3.	If the source experiences any deviations from the applicable requirements during the reporting period, include a description of deviations, the time periods during which the deviations occurred, and the corrective actions taken.

g.	The Permittee must keep a copy of each notification and report that was submitted to comply with 40 CFR 63, Subpart JJJJJJ and this section and all documentation supporting any Initial Notification or Notification of Compliance Status that was submitted. [40 CFR 63.11225(c)(1)]

h.	The Permittee must keep records to document compliance with the requirements of Condition III as follows [40 CFR 63.11225(c)(2)]:

1.	Records must identify each boiler, the date of tune-up, the procedures followed for tune-up, and the manufacturer’s specifications to which the boiler was tuned.

2.	Records documenting the fuel type(s) used monthly by each boiler, including, but not limited to, a description of the fuel, including whether the fuel has received a non-waste determination by the Permittee or EPA, and the total fuel usage amount with units of measure.

i.	The Permittee must keep records of the occurrence and duration of each malfunction of each boiler, or of any associated air pollution control and monitoring equipment. [40 CFR 63.11225(c)(4)]

j.	The Permittee must keep records of all actions taken during periods of malfunction to minimize emissions in accordance with the general duty to minimize emissions in 40 CFR 63.11205(a), including corrective actions to restore the malfunctioning boiler, air pollution control, or monitoring equipment to its normal or usual manner of operation. [40 CFR 63.11225(c)(5)]

If you have any questions, please call me at (202) 535-1747 or John Nwoke at (202) 724-7778.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:JCN