July 8, 2014

Stephen K. Hurley

Manager, Facility Services

United States Postal Service Headquarters- L’Enfant Plaza

475 L’Enfant Plaza Southwest

Washington, DC 20260-0004

RE:	Permits to Operate Two Dual Fuel Fired Boilers at 475 L’Enfant Plaza Southwest

Dear Mr. Hurley:

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit from the District Department of the Environment (the Department) shall be obtained before any person can construct and operate a stationary source in the District of Columbia. The application of the United States Postal Service (the Permittee) to operate the listed 10 MMBTU/hr dual-fueled boilers (natural gas and No. 2 fuel oil) located at 475 L’Enfant Plaza Southwest, Washington DC, have been reviewed:

| Permit No. | Equipment Size (MMBTU/hr | Manufacturer | Serial Number |
| --- | --- | --- | --- |
| 6804 | 10.0 | Cleaver Brooks | BT 04021-1-1 |
| 6805 | 10.0 | Cleaver Brooks | BT 04021-1-2 |

Based on the submitted plans and specifications as detailed in the applications received on October 17, 2013, the application has been reviewed and the operation of the boilers is permitted, subject to the following conditions:

I.	General Requirements:

  - The approval is issued pursuant to the applicable air pollution control requirements of 20 DCMR for the construction and operation of the steam boilers.

b.	This set of permit will expire on July 7, 2019.  If continued operation after this date is desired, the owner or operator shall submit application for renewal by April 7, 2019. [20 DCMR 200.4]

c.	Operation of equipment under the authority of this permit shall be considered acceptance of its terms and conditions.

- The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1.	Enter upon the Permittee’s premises where a source or emission units are located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

- This permit shall be kept on the premises and produced upon request.

- Failure to comply with the provisions of this permit may be grounds for suspension or revocation. [20 DCMR 202.2]

II.	Emission Limitations:

  - Each of the two identical 10.0 million BTU per hour Cleaver Brooks dual-fueled boilers shall not emit pollutants in excess of those rates specified in the following table [20 DCMR 201]:

| Boiler Emission Limits |
| --- |
| Pollutant | Short-Term Limit (Natural Gas) (lb/hr) | Short-Term Limit (#2 Fuel Oil) (lb/hr) |
| Carbon Monoxide (CO) | 0.80 | 0.365 |
| Oxides of Nitrogen (NOx) | 0.950 | 1.46 |
| Total Particulate Matter (PM Total)* | 0.070 | 0.240 |
| Sulfur Dioxide (SO2) | 0.005 | 0.52 |

*PM Total includes both filterable and condensable fractions.

  - b.	Visible emissions shall not be emitted into the outdoor atmosphere from the boilers, except that discharges not exceeding forty percent (40%) opacity (unaveraged) shall be permitted for two (2) minutes in any sixty (60) minute period and for an aggregate of twelve (12) minutes in any twenty-four hour (24 hr.) period during start-up, cleaning, adjustment of combustion controls, or malfunction of the equipment [20 DCMR 606.1]

c.	An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1]

d.	Total suspended particulate matter (TSP) emissions from each of the boilers shall not exceed 0.102 pound per million BTU. [20 DCMR 600.1]

III.	Operational Limitations:

  - a.	The primary fuel for the boilers shall be natural gas. [20 DCMR 201]

  - b. 	The back-up fuel for the boilers shall be #2 fuel oil containing no greater than 0.0015% sulfur by weight. [20 DCMR 201, 20 DCMR 205.1, 20 DCMR 801.1 and 40 CFR 60.42c(d)] Note that this is a streamlined permit requirement. 40 CFR 60.42c(d) is more stringent than 20 DCMR 801.1, therefore compliance with this requirement will also show compliance with 20 DCMR 801.1. In the permit application, the Permittee requested a limit that is more stringent than both regulatory limits, thus it has been included as the sole limit in the permit pursuant to 20 DCMR 201.

c.	   The boilers shall operate on No. 2 fuel oil only for the following reasons: [20 DCMR 201, 40 CFR 63.11195(e) and 40 CFR 63.11237]

1.	During periods of gas supply emergencies;

2.	During periods of gas curtailment; or

3.	For periodic testing on liquid fuel not to exceed a combined total of 48 hours

during any calendar year.

e.	The boilers shall be operated at all times in a manner consistent with the manufacturer’s specifications for the equipment. [20 DCMR 201]

f.	At all times, including periods of startup, shutdown, and malfunction, the owner or operator shall, to the extent practicable, maintain and operate each boiler in a manner consistent with good air pollution control practice for minimizing emissions.  Determination of whether acceptable operating procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source. [20 DCMR 201]

IV.	Monitoring and Testing Requirements:

a.	At least once during the term of this permit, the Permittee shall conduct performance testing on each boiler using each of the fuels (natural gas and No. 2 fuel oil), to determine compliance with Conditions II(a) (except SO2) and (d) and shall furnish the Department with a written report of the results of such performance test in accordance with the following requirements [20 DCMR 502]:

1.	One (1) original and one (1) copy of the test protocol shall be submitted to the following address a minimum of thirty (30) days in advance of the proposed test date.  The test shall be conducted in accordance with Federal and District requirements.

Chief, Compliance and Enforcement Branch

Air Quality Division

1200 First Street NE

5th Floor

Washington, DC 20002

2.	The test protocol shall be approved by the Department prior to initiating any testing.  Upon approval of the test protocol, the Company shall finalize the test date with the assigned inspector in the Compliance and Enforcement Branch.  The District must have the opportunity to observe the test for the results to be considered for acceptance.

3.	The final results of the testing shall be submitted to the Department within sixty (60) days of the test completion.  One (1) original and one (1) copy of the test report shall be submitted to the address in Condition IV (a) (1) above.

4.	The final report of the results shall include the emissions test report (including raw data from the test) as well as a summary of the test results and a statement of compliance or non-compliance with permit conditions to be considered valid.  The summary of results and statement of compliance or non-compliance shall contain the following information:

A.	A statement that the owner or operator has reviewed the report from the emissions testing firm and agrees with the findings.

B.	Permit number(s) and condition(s) which are the basis for the compliance evaluation.

C.	Summary of results with respect to the permit condition.

D.	Statement of compliance or non-compliance with each permit condition.

5.	The results must demonstrate to the Department’s satisfaction that the emission unit is operating in compliance with the applicable regulations and conditions of this permit; if the final report of the test results shows non-compliance the owner or operator shall propose corrective action(s).  Failure to demonstrate compliance through the test may result in enforcement action.

b.	The owner or operator shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested.  [20 DCMR 502.1]

c.	At least once per quarter, during operation of each boiler using natural gas and at least once per week when burning No. 2 fuel oil, the Permittee shall conduct visual observations of the emissions from the boilers.  If no operations are occurring for a given boiler during a given quarter, this shall be so noted.  If emissions are visible, the Permittee shall make arrangements for prompt visible emissions testing by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A). Such a test shall consist of a minimum of 30 minutes of opacity observations for the boiler in question and shall be performed while firing the same fuel as was in use when the visible emissions were observed.

d.	Regardless of whether or not emissions are observed pursuant to Condition IV(c) of this permit, the Permittee shall conduct a minimum of one visible emissions test of each boiler each year for each fuel burned that year.  If the only combustion of a given fuel burned since the last test was burned during periodic testing required by this permit, no visible emission test for that fuel will be required under this condition. Such a test program shall consist of a minimum of 30 minutes of opacity observations of each boiler firing each fuel and shall be performed by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).

e.	Unless more frequent testing is specified elsewhere in this permit, the Permittee shall sample and test the fuel oil burned in the boilers at least once each calendar quarter or at the time of each fuel delivery, whichever is less frequent.  For each sample, the Permittee must provide: [20 DCMR 502]

1.	The fuel oil grade;

2.	The weight percent sulfur of the fuel oil as determined using ASTM test method

D-4294 or D-5453 or other method approved in advance by the Department;

3.	The date and time the sample was taken;

4.	The name, address, and telephone number of the laboratory that analyzed the

sample; and

5.	The type of test or test method performed.

In lieu of sampling and testing fuel oil each quarter for each of these data, the Permittee may obtain these data from the fuel supplier at the time of delivery and submit fuel receipts and fuel supplier certifications for all fuel deliveries that provide all of the above quality of fuel data as well as the name of the fuel supplier, the date of delivery, a statement from the oil supplier that the oil complies with the specifications under the definition of distillate oil (see 40 CFR 60.41c), and the sulfur content of the oil [40 CFR 60.48c(f)]

Note that the sulfur content data obtained from the fuel supplier must be the results of specific tests of the fuel at hand.  General fuel specifications are not acceptable for this datum.

If any of these data cannot be obtained from the fuel supplier, it is the responsibility of the Permittee to sample the fuel and have it analyzed to obtain the required data.

V.	Record Keeping and Reporting Requirements:

a.	The Permittee shall keep records of the results of all emissions testing required for the

boilers pursuant to Conditions IV(a) and (b) of this permit for a period of not less than five (5) years. [20 DCMR 500.8 and 20 DCMR 201]

b.	The Permittee shall keep records of the results of all fuel sulfur testing and fuel supplier certifications obtained pursuant to Condition IV(e) for a period of not less than three (3) years. [20 DCMR 500.8]

c.	The Permittee shall maintain records of all visible emissions monitoring performed pursuant to Condition IV(c), for a period of not less than three (3) years, including notes indicating when no observations were performed as a result of not operating of the boiler that week.  These records shall be maintained in an organized fashion, shall include the identity of the person performing the monitoring, and shall be readily available for inspection by the District. [20 DCMR 500.8]

d.	The Permittee shall maintain records of all Method 9 visible emissions testing performed pursuant to Conditions IV(c) and (d) for a period of not less than five (5) years.  These records shall also include the identity of the person performing the visible emissions testing and documentation of his/her Method 9 certification.  These records shall include documentation indicating whether the results show compliance with Condition II(b). [20 DCMR 500.8]

e.	The Permittee shall maintain records of all instances of boiler operation using No. 2 fuel oil, including the reason for operation using that fuel and the number of hours the boiler is operated using that fuel.  These data shall be maintained for a period of not less than three (3) years. [20 DCMR 500.8]

f.	The Permittee shall maintain records of the amount of each fuel used each month in the boilers.  These data shall be maintained for a period of not less than three (3) years. [20 DCMR 500.8]

If you have any questions, please call me at (202) 535-1747 or Olivia Achuko at (202) 535-2997.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:OA