June 30, 2015

Jonathan Kayne, Interim Director

District of Columbia Department of General Services

2000 14th Street, NW, 8th Floor

Washington, DC 20009

RE:	Permit (#6993) to Operate a 750 kW Onan Diesel-Fired Emergency Generator Set in the ACCC Building of the D.C. General Health Campus at 1900 Massachusetts Avenue SE, Washington, DC

Dear Mr. Kayne:

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit from the District Department of the Environment (the Department) shall be obtained before any person can construct and operate a stationary source in the District of Columbia. The application of the District of Columbia Department of General Services (the Permittee) to operate a 750 kWe Onan emergency generator set with a 1,006 bhp diesel-fired engine, located at the ACCC Building of the D.C. General Health Campus at 1900 Massachusetts Avenue SE, Washington, DC, per the submitted plans and specifications, received by email on February 27, 2015 and subsequently in hard copy on April 2, 2015 is hereby approved, subject to the following conditions:

I.	General Requirements:

a.	The emergency generator set shall be maintained and operated in accordance with the air pollution control requirements of 20 DCMR.

b.	This permit expires on June 29, 2020 [20 DCMR 200.4].  If continued operation after this date is desired, the owner or operator shall submit a renewal application by March 29, 2020.

c.	Operation of equipment under the authority of this permit shall be considered acceptance of its terms and conditions.

d.	The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1.	Enter upon the Permittee’s premises where a source or emission unit is located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

e.	This permit shall be kept on the premises and produced upon request.

- Failure to comply with the provisions of this permit may be grounds for suspension or revocation. [20 DCMR 202.2]

- If not already completed by the date of issuance of this permit, within twelve (12) months of issuance of this permit to operate, the Permittee shall submit a complete application to modify the facility’s Title V operating permit to include the requirements of this permit [20 DCMR 301.1(a)(3)].  This application is due by June 29, 2016.

II.	Emission Limitations:

a.	Visible emissions shall not be emitted into the outdoor atmosphere from this generator, except that discharges not exceeding forty percent (40%) opacity (unaveraged) shall be permitted for two (2) minutes in any sixty (60) minute period and for an aggregate of twelve (12) minutes in any twenty-four hour (24 hr.) period during start-up, cleaning, adjustment of combustion controls, or malfunction of the equipment [20 DCMR 606.1].

b.	An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1]

III.	Operational Limitations:

  - a.	The emergency generator shall not be operated in excess of 500 hours in any given 12 month period.  If operation beyond 500 hours is desired, the owner or operator shall submit an application to amend this permit to comply with the conditions of 20 DCMR 805 and shall obtain the Department’s approval of such application prior to initiating such operation.

b.	With the exceptions specified in Condition III(c), the emergency generator shall be operated only during emergencies as follows:

1.	An electrical power outage due to: a failure of the electrical grid; on-site disaster; local equipment failure; or public service emergencies such as flood, fire, natural disaster, or severe weather conditions (e.g. hurricane, tornado, blizzard, etc.);

2.	For period of up to 15 hours per calendar year when there is a deviation of voltage or frequency from the electrical provider to the premises of 5 percent or more below standard voltage or frequency such that the equipment being supported cannot be safely or effectively operated; or

3.	When a sudden, unexpected event occurs that, if not immediately attended to, presents a safety or public health hazard, is necessary to protect equipment from damage, or is necessary to avoid imposing an unreasonable financial burden.  An emergency includes operations necessitated by non-routine failures of equipment, but it does not include voluntary demand reductions covered by Condition III(f).

c.	The emergency generator may be operated for the purpose of maintenance checks and readiness testing for a period not to exceed one hundred (100) hours per calendar year. Any such operation shall be considered as part of the 500 hours allowed under Condition III(a) above. [20 DCMR 201]

d.	The emergency generator shall fire only diesel fuel which contains a maximum sulfur content of 15 ppm (0.0015 percent by weight) and either a minimum cetane index of 40 or a maximum aromatic content of 35 volume percent. [20 DCMR 201]

e.	The emergency generator shall be operated and maintained in accordance with the recommendations of the equipment manufacturer or to industry standards for similar models if manufacturer specifications are unavailable.  [20 DCMR 201]

f.	The emergency generator shall not be operated in conjunction with a voluntary demand-reduction program or any other interruptible power supply arrangement with a utility, other market participant, or system operator.

g.	At all times, including periods of startup, shutdown, and malfunction, the owner shall, to the extent practicable, maintain and operate the units in a manner consistent with good air pollution control practice for minimizing emissions.  Determination of whether acceptable operating procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source.

IV.	Monitoring and Testing Requirements:

a.	The owner or operator shall monitor the date, time, duration, and reason for each emergency generator startup to ensure compliance with Condition III(a), (b), (c) and (f).

b.	In order to ensure compliance with Condition III(a), the owner or operator shall monitor the total hours of operation each month with the use of properly functioning, non-resettable hour metering device or by tracking the sum of the duration of each instance of operation each month.

c.	The owner or operator shall test fuel oil as necessary to show compliance with Conditions III(d) and V(c) in accordance with appropriate ASTM methods. [20 DCMR 502.6]

d.	The owner or operator shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested.  [20 DCMR 502.1]

V.	Record Keeping Requirements:

a.	The following information shall be recorded, initialed, and maintained in a log at the facility for a period not less than five (5) years [20 DCMR 500.8, 20 DCMR 302.1 (c)(2)(B)]:

1.	The date, time, duration, and reason for each start-up of the emergency generator; (Note that if the unit is operated due to a deviation in voltage from the utility pursuant to Condition III(b)(2), this shall be specifically noted.)

2.	The total hours of operation for each month and the cumulative 12-month rolling period shall be calculated and recorded within 15 days of the end of each calendar month for the previous month and the 12-month period ending at the end of that month;

3.	The total hours of operation for maintenance checks and readiness testing pursuant to Condition III(c) each month, and totaled for each calendar year by January 15 of each year for the previous calendar year.

4.	The total hours of operation due to a deviation in voltage from the utility pursuant to Condition III(b)(2) each calendar year, totaled by January 15 of each calendar year for the previous calendar year;

5.	Records of the maintenance performed on the unit;

6.	Records of the results of any visible emissions monitoring performed;

7.	Records of the occurrence and duration of each malfunction of operation; and

8.	Records of the actions taken during periods of malfunction to minimize emissions, including corrective actions to restore malfunction process and air pollution control and monitoring equipment to its normal or usual manner of operation.

b.	The owner or operator shall maintain a copy of the emergency generator’s manufacturer’s maintenance and operating recommendations at the facility.  If such documentation is unavailable, the owner or operator shall maintain documentation of the industry standards to which the unit is being maintained. [20 DCMR 501]

c.	For each delivery of diesel fuel, the owner or operator shall maintain one of the following:

1.	A fuel delivery receipt containing the date, fuel type, and amount of the delivery and certification from the fuel supplier that the fuel delivered was tested in accordance with an appropriate ASTM method (specified in the certification) and met the requirements of Condition III(d); or

2.	A fuel delivery receipt and documentation of sampling and analysis containing the following information:

A.	The fuel oil type and the ASTM method used to determine the type (see the definition of distillate oil in 40 CFR 60.41c for appropriate ASTM methods);

B.	The weight percent sulfur of the fuel as determined using ASTM test method D-4294 or D-5453 or other methods approved in advance by the Department;

C.	The date and time the sample was taken;

D.	The name, address, and telephone number of the laboratory that analyzed the sample; and

E.	The test method used to determine the sulfur content.

If you have any questions, please call me at (202) 535-1747 or John Nwoke at (202) 724-7778.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:JCN