April 26, 2016

Brian Coulter

Managing Member

JBG/Federal Center, L.L.C.

1200 New Jersey Avenue SE

Washington, DC 20590

Re: 	Permit Nos. 7022 through 7025 to Operate Four Dual Fuel Boilers at the United States Department of Transportation (USDOT) Headquarters

Dear Mr. Coulter:

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit from the Department of Energy and Environment (“the Department”) shall be obtained before any person can construct and operate a stationary source in the District of Columbia. The applications of JBG/Federal Center, L.L.C. (“the Permittee”)  to operate four (4) dual-fuel fired boilers (listed below) located at the United States Department of Transportation (USDOT) Headquarters at 1200 New Jersey Avenue SE, Washington, DC 20590 has been reviewed:

| Permit # | Equipment Type | Equipment Size (HHV heat input basis) | Fuel Type | Equip ID |
| --- | --- | --- | --- | --- |
| 7022 | Boiler - AJAX - CU-1 | 10.5 MMBTU/hr | Gas & Diesel | BLR-1-East |
| 7023 | Boiler - AJAX - CU-2 | 10.5 MMBTU/hr | Gas & Diesel | BLR-2-East |
| 7024 | Boiler - AJAX - CU-3 | 10.5 MMBTU/hr | Gas & Diesel | BLR-1-West |
| 7025 | Boiler - AJAX - CU-4 | 10.5 MMBTU/hr | Gas & Diesel | BLR-2-West |

Based on the submitted plans and specifications as detailed in the air permit application that has been updated several times since an original submission in August 2011, most recently with submissions dated April 15, 2015 and September 22, 2015, the Permittee’s applications are hereby approved for the operation of the boilers, subject to the following conditions:

I.	General Requirements:

  - This approval is issued pursuant to the applicable air pollution control requirements of 20 DCMR for the construction and operation of the external combustion equipment.

b.	This set of permits will expire on April 25, 2021.  If continued operation after this date is desired, the Permittee shall submit application for renewal by January 25, 2021. [20 DCMR 200.4]

c.	Operation of equipment under the authority of these permits shall be considered acceptance of their terms and conditions.

- The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1.	Enter upon the Permittee’s premises where a source or emission unit is located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

- These permits shall be kept on the premises and produced upon request.

- Failure to comply with the provisions of these permits may be grounds for suspension or revocation. [20 DCMR 202.2]

- Within twelve (12) months of issuance of these permits to operate, the Permittee shall submit a complete application to obtain a Title V operating permit unless the Department has established a synthetic minor operating permit program by that time, in which case the Permittee may opt to apply for coverage under that program, as applicable. [20 DCMR 301.1(a)(2)]

II.	Emission Limitations:

  - Each of the four (4) identical 10.5 million BTU per hour (MMBTU/hr) AJAX dual fuel-fired boilers shall not emit pollutants in excess of the rates specified in the following table [20 DCMR 201]:

| Boiler Emission Limits |
| --- |
| Pollutant | Short-Term Limit (Natural Gas) (lb/hr) | Short-Term Limit (No. 2 Fuel Oil/Diesel) (lb/hr) |
| Carbon Monoxide (CO) | 0.84 | 0.38 |
| Oxides of Nitrogen (NOx) | 1.0 | 1.50 |
| Total Particulate Matter (PM Total)* | 0.076 | 0.25 |
| Sulfur Dioxide (SO2) | 0.006 | 0.02 |

*PM Total includes both filterable and condensable fractions.  Note that compliance with Conditions III(a)-(c) will be considered compliance with these PM Total standards, unless other credible evidence of a violation is identified.

  - b.	Visible emissions shall not be emitted into the outdoor atmosphere from the boilers, except that discharges not exceeding forty percent (40%) opacity (unaveraged) shall be permitted for two (2) minutes in any sixty (60) minute period and for an aggregate of twelve (12) minutes in any twenty-four hour (24 hr.) period during start-up, cleaning, adjustment of combustion controls, or malfunction of the equipment [20 DCMR 606.1]

c.	An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1]

d.	Total suspended particulate matter (TSP) emissions from each of the boilers shall not exceed 0.10 pound per million BTU. [20 DCMR 600.1]

III.	Operational Limitations:

a.	Natural gas shall be used as the primary fuel in the boilers.  No. 2 fuel oil or diesel fuel shall be used only in accordance with Condition III(d). No other fuels are approved for use.

b.	The back-up fuel for the boilers shall be No. 2 fuel oil or diesel fuel that meets the following requirements [20 DCMR 801]:

    - At no time shall the fuel contain greater than 0.081 weight percent sulfur  [40 CFR 60.42c(d) and 20 DCMR 201] Note that this is a streamlined permit condition; use of fuel with a sulfur content no greater than 0.081% by weight as requested in the application will ensure compliance with the less stringent requirements of 40 CFR 60.42c(d) and 20 DCMR 801.1.;

    - On an after July 1, 2016, no fuel oil shall be purchased for use in these boilers that contains in excess of five hundred parts per million (500 ppm) by weight, or five one-hundredths percent (0.05%) by weight;

    - On and after July 1, 2018, no fuel oil shall be purchased for use in these boilers that contains more than fifteen parts per million (15 ppm) or fifteen ten-thousandths percent (0.0015%) by weight of sulfur, except as specified in Condition III(b)(4);

    - When EPA temporarily suspends or increases the applicable limit or percentage by weight of sulfur content of fuel required or regulated by EPA by granting a waiver in accordance with Clean Air Act § 211(c)(4)(C) provisions, the federal waiver shall apply to corresponding limits for fuel oil in the District as set forth in Condition III(b)(3);

    - If a temporary increase in the applicable limit of sulfur content is granted under Condition III(b)(4), the suspension or increase in the applicable limit will be granted for the duration determined by EPA;

c.	   The boilers shall operate on No. 2 fuel oil or diesel fuel only for the following reasons: [20 DCMR 201, 40 CFR 63.11195(e) and 40 CFR 63.11237]

1.	During periods of gas supply emergencies;

2.	During periods of gas curtailment; or

3.	For periodic testing on liquid fuel not to exceed a combined total of 48 hours

during any calendar year.

d.	The maximum hours of operation of the three boilers, in aggregate, shall be 17,520 hours per 12-month rolling period.

e.		One of the four boilers is a redundant boiler at all times that can only operate if one of the other boilers is shut down. At no time shall all four boilers be operated at once.

f.	The boilers shall be operated at all times in a manner consistent with the manufacturer’s specifications for the equipment. [20 DCMR 201]

g.	At all times, including periods of startup, shutdown, and malfunction, the Permittee shall, to the extent practicable, maintain and operate each boiler in a manner consistent with good air pollution control practice for minimizing emissions.  Determination of whether acceptable operating procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source. [20 DCMR 201]

IV.	Monitoring and Testing Requirements:

a.	At least once during the term of this permit, the Permittee shall conduct performance testing on each boiler using each of the fuels (natural gas and diesel), to determine compliance with Conditions II(a) (except PM Total and SO2) and (d) and shall furnish the Department with a written report of the results of such performance test in accordance with the following requirements [20 DCMR 502]:

1.	One (1) original and one (1) copy of the test protocol shall be submitted to the following address a minimum of thirty (30) days in advance of the proposed test date.  The test shall be conducted in accordance with Federal and District requirements.

Chief, Compliance and Enforcement Branch

Air Quality Division

1200 First Street NE

5th Floor

Washington, DC 20002

2.	The test protocol shall be approved by the Department prior to initiating any testing.  Upon approval of the test protocol, the Company shall finalize the test date with the assigned inspector in the Compliance and Enforcement Branch.  The District must have the opportunity to observe the test for the results to be considered for acceptance.

3.	The final results of the testing shall be submitted to the Department within sixty (60) days of the test completion.  One (1) original and one (1) copy of the test report shall be submitted to the address in Condition IV(a) (1) above.

4.	The final report of the results shall include the emissions test report (including raw data from the test) as well as a summary of the test results and a statement of compliance or non-compliance with permit conditions to be considered valid.  The summary of results and statement of compliance or non-compliance shall contain the following information:

A.	A statement that the Permittee has reviewed the report from the emissions testing firm and agrees with the findings.

B.	Permit number(s) and condition(s) which are the basis for the compliance evaluation.

C.	Summary of results with respect to the permit condition.

D.	Statement of compliance or non-compliance with each permit condition.

5.	The results must demonstrate to the Department’s satisfaction that the emission unit is operating in compliance with the applicable regulations and conditions of this permit; if the final report of the test results shows non-compliance the Permittee shall propose corrective action(s).  Failure to demonstrate compliance through the test may result in enforcement action.

b.	The Permittee shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested.  [20 DCMR 502.1]

c.	At least once per quarter, during operation of each boiler using natural gas and at least once per week when burning No. 2 fuel oil or diesel, the Permittee shall conduct visual observations of the emissions from the boilers.  If no operations are occurring for a given boiler during a given quarter, this shall be so noted.  If emissions are visible, the Permittee shall make arrangements for prompt visible emissions testing by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A). Such a test shall consist of a minimum of 30 minutes of opacity observations for the boiler in question and shall be performed while firing the same fuel as was in use when the visible emissions were observed.

d.	Regardless of whether or not emissions are observed pursuant to Condition IV(c) of this permit, the Permittee shall conduct a minimum of one visible emissions test of each boiler each year for each fuel burned that year.  If the only combustion of a given fuel burned since the last test was burned during periodic testing required by this permit, no visible emission test for that fuel will be required under this condition. Such a test program shall consist of a minimum of 30 minutes of opacity observations of each boiler firing each fuel and shall be performed by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).

The Air Quality Division (AQD) Compliance and Enforcement Branch shall be notified at least fifteen (15) days in advance of the testing required by this condition so as to be given the opportunity to observe this testing.  The notification shall be sent to the following address:

Chief, Compliance and Enforcement Branch

Air Quality Division

Department of Energy and Environment

1200 First Street NE, 5th Floor

Washington DC 20002

e.	To show compliance with Condition III(b), the Permittee shall obtain and maintain records in accordance with Condition V(d).  Additionally, the Department reserves the right to require supplemental sampling and testing of the fuel oil to confirm the certifications provided by the fuel supplier.  If such sampling is required, it shall be performed in accordance with the following methods:

1.	To obtain fuel samples:

A.	ASTM D 270, “Standard Method of Sampling Petroleum and Petroleum Products;”

B.	ASTM D 4057, “Practice for Manual Sampling of Petroleum and Petroleum Products;” or

C.	ASTM D 4177, “Standard Practice for Automatic Sampling of Petroleum and Petroleum Products;”

2.	To determine the fuel oil grade: ASTM D 396, “Standard Specification for Fuel Oils;”

3.	To determine the sulfur concentration of fuels:

A.	ASTM D 129, “Standard Test Method for Sulfur in Petroleum Products (General Bomb Method)”;

B.	ASTM D 1266, “Standard Test Method for Sulfur in Petroleum Products (Lamp Method)”;

C.	ASTM D 1552, “Standard Test Method for Sulfur in Petroleum Products (High-Temperature Method”;

D.	ASTM D 2622, “Standard Test Method for Sulfur in Petroleum Products by Wavelength Dispersive X-Ray Fluorescence Spectrometry”;

E.	ASTM D 4294, “Test Method for Sulfur in Petroleum and Petroleum Products by Energy Dispersive X-ray Fluorescence Spectrometry;” or

F.	ASTM D 5453, “Standard Test Method for Determination of Total Sulfur in Light Hydrocarbons, Spark Ignition Engine Fuel, Diesel Engine Fuel, and Engine Oil by Ultraviolet Fluorescence;” and

4.	Other methods developed or approved by the Department or EPA.

f.	The Permittee shall monitor the operation of the boilers in a manner consistent with a good preventive maintenance program.

g.	The Permittee shall monitor the type and amount of fuel burned in the boilers, along with the reason for and duration of any use of No. 2 fuel oil.

h.	The Permittee shall monitor the total number of hours each calendar month that each boiler is operated.  These shall be summed each month for the four boilers and these sums shall be tracked in a rolling 12-month format to ensure compliance with Condition III(d).

i.	The Permittee shall monitor which boilers are in use at any given time to ensure compliance with Condition III(e).

j.	The Permittee shall monitor the stack outlets and identify any visible emissions to ensure that if they occur, the problem is identified and repaired.

V.	Record Keeping and Reporting Requirements:

The following information shall be recorded and maintained in a log at the facility for

a period not less than five (5) years from the date the information is obtained. [20 DCMR 302.1(c)(2)(B) and 20 DCMR 500.8]

a.	The Permittee shall keep records of the results of all emissions testing required for the

boilers pursuant to Conditions IV(a) and (b) of this permit. [20 DCMR 500.8 and 20 DCMR 201]

b.	The Permittee shall maintain records of all visible emissions monitoring performed pursuant to Condition IV(c), including notes indicating when no observations were performed as a result of not operating of the boiler that week.  These records shall be maintained in an organized fashion, shall include the identity of the person performing the monitoring, and shall be readily available for inspection by the District. [20 DCMR 500.8]

c.	The Permittee shall maintain records of all Method 9 visible emissions testing performed pursuant to Conditions IV(c) and (d).  These records shall also include the identity of the person performing the visible emissions testing and documentation of his/her Method 9 certification.  These records shall include documentation indicating whether the results show compliance with Condition II(b). [20 DCMR 500.8]

d.	For each delivery of No. 2 fuel oil, the Permittee shall obtain from the fuel supplier an electronic or paper record of the following fuel data (Note that a product transfer document that meets federal requirements and contains this these data, such as a Bill of Lading, may be used to meet these requirements and shall be considered a certification that the information is accurate.):

1.	The date of delivery;

2.	The name, address, and telephone number of the transferor (the fuel supplier);

3.	The name and address of the transferee (the Permittee or Permittee’s representative);

4.	The volume of fuel oil being sold or transferred;

5.	The fuel oil grade; and

6.	The sulfur content of the fuel oil as determined using the sampling and testing methods specified in Condition IV(e), which may be expressed as the maximum allowable sulfur content.

e.	The Permittee shall maintain records of all instances of boiler operation using No. 2 fuel oil or diesel fuel, including the reason for operation using that fuel and the number of hours the boiler is operated using that fuel. [20 DCMR 500.8]

f.	The Permittee shall maintain records of the amount of each fuel used each month in the boilers. These data may be maintained as a total amount of each fuel for all boilers combined if there are not separate fuel meters on each boiler.  These monthly data shall, in turn, be maintained in a calendar year total sum format.  [20 DCMR 500.8]

g.	The Permittee shall maintain records of the number of hours each boiler is operated each month. These data shall be summed each month.  These resultant sums shall be maintained in a 12-month rolling sum format to determine compliance with Condition III(d).

h.	The Permittee shall keep records of all maintenance performed on the boilers so as to document compliance with Conditions III(e) and (f).  These records shall be initialed to attest to their accuracy.

If you have any questions, please call me at (202) 535-1747 or Olivia Achuko at (202) 535-2997.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:OA