November 22, 2016

Marc Edelman

Senior Vice President, Operations

Providence Hospital

1150 Varnum Street NE

Washington, DC 20017

Re: 	Permit No 7088 to Construct and Operate One 24.80 MMBTU/hr Dual Fuel-Fired Boiler

Dear Mr. Edelman:

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit from the Department of Energy and Environment (“the Department”) shall be obtained before any person can construct and operate a stationary source in the District of Columbia. The application of Providence Hospital (“the Permittee”) to construct and operate one (1) dual fuel-fired (natural gas and #2 fuel oil) 24.80 MMBtu per hour boiler located at the Providence Hospital at 1150 Varnum Street, NE Washington, DC 20017 has been received.

Based on the submitted plans and specifications as detailed in the air permit application received on March 11, 2016 as revised by the latest updated application received on October 19, 2016, the application is hereby approved, and the construction and operation of the boiler is permitted, subject to the following conditions:

I.	General Requirements:

  - This approval is issued pursuant to the applicable air pollution control requirements of 20 DCMR for the construction and operation of external combustion equipment.

b.	This permit will expire on November 21, 2021.  If continued operation after this date is desired, the Permittee shall submit application for renewal by August 21, 2021. [20 DCMR 200.4]

c.	Construction and operation of equipment under the authority of this permit shall be considered acceptance of its terms and conditions.

- The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1.	Enter upon the Permittee’s premises where a source or emission unit is located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

- This permit shall be kept on the premises and produced upon request.

- Failure to comply with the provisions of this permit may be grounds for suspension or revocation. [20 DCMR 202.2]

- This unit replaces Boiler 1 (Emission Unit ID 17034) in Title V permit 008-R2, issued on July 1, 2015.  Within twelve (12) months of issuance of this permit, the Permittee shall submit a complete permit application to request a modification of the Title V operating permit to incorporate the new boiler and remove the replaced boiler. [20 DCMR 301.1(a)(2) and (3)]

II.	Emission Limitations:

  - This 24.80 million BTU per hour (MMBTU/hr) dual fuel-fired boiler shall not emit pollutants in excess of the rates specified in the following table [20 DCMR 201]:

| Boiler Emission Limits |
| --- |
| Pollutant | Short-Term Limit (Natural Gas) (lb/hr) | Short-Term Limit (No. 2 Fuel Oil) (lb/hr) |
| Carbon Monoxide (CO) | 1.810 | 0.952 |
| Oxides of Nitrogen (NOx) | 0.868 | 2.808 |
| Particulate Matter less than 10 microns in aerodynamic diameter (PM10)1 | 0.188 | 0.562 |
| Sulfur Dioxide (SO2) | 0.015 | 0.048 |

1PM10 includes both filterable and condensable fractions.

  - b.	Visible emissions shall not be emitted into the outdoor atmosphere from the boiler, except that discharges not exceeding forty percent (40%) opacity (unaveraged) shall be permitted for two (2) minutes in any sixty (60) minute period and for an aggregate of twelve (12) minutes in any twenty-four hour (24 hr.) period during start-up, cleaning, adjustment of combustion controls, or malfunction of the equipment [20 DCMR 606.1]

c.	An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1]

d.	Total suspended particulate matter (TSP) emissions from the boiler shall not exceed 0.08 pound per million BTU. [20 DCMR 600.1]

- Emissions shall not exceed those achieved with the performance of annual combustion adjustments on the boiler for each fuel. To show compliance with this condition, the Permittee shall, each calendar year, perform adjustments of the combustion process of the boiler with the following characteristics [20 DCMR 805.1(a)(4) and 20 DCMR 805.8(a) and (b)]:

    - Inspection, adjustment, cleaning or replacement of fuel burning equipment, including the burners and moving parts necessary for proper operation as specified by the manufacturer;

    - Inspection of the flame pattern or characteristics and adjustments necessary to minimize total emissions of NOx and, to the extent practicable, minimize emissions of CO;

    - Inspection of the air-to-fuel ratio control system and adjustments necessary to ensure proper calibration and operation as specified by the manufacturer; and

    - Adjustments shall be made such that the maximum emission rate for any contaminant does not exceed the maximum allowable emission rate as set forth in Condition II(a).

III.	Operational Limitations:

a.	Natural gas shall be used as the primary fuel in the boiler.  No. 2 fuel oil shall be used only in accordance with Conditions III(b) and (c). No other fuels are approved for use. [20 DCMR 201]

b.	The back-up fuel for the boiler shall be No. 2 fuel oil that meets the following requirements [20 DCMR 201, 20 DCMR 801, and 40 CFR 60.42]:

1.	No fuel oil shall be purchased for use in the boiler that contains more than fifteen parts per million (15 ppm) or fifteen ten-thousandths percent (0.0015%) by weight of sulfur, except as specified in Conditions III(b)(2) and (3);

2.	When EPA temporarily suspends or increases the applicable limit or percentage by weight of sulfur content of fuel required or regulated by EPA by granting a waiver in accordance with Clean Air Act § 211(c)(4)(C) provisions, the federal waiver shall apply to corresponding limits for fuel oil in the District as set forth in Condition III(b)(1); and

3.	If a temporary increase in the applicable limit of sulfur content is granted under Condition III(b)(2), the suspension or increase in the applicable limit will be granted for the duration determined by EPA and the sulfur content may not exceed 500 ppm by weight.

c.	   The boiler shall operate on No. 2 fuel oil only for the following reasons: [20 DCMR 201, 40 CFR 63.11195(e) and 40 CFR 63.11237]

1.	During periods of gas supply emergencies;

2.	During periods of gas curtailment; or

3.	For periodic testing on #2 fuel not to exceed a combined total of 48 hours

during any calendar year.

d.	The boiler shall operate on No. 2 fuel oil in accordance with Condition III(c) for no more than 11,320 hours in any consecutive 12-month period. [20 DCMR 201]

e.	The boiler shall be operated at all times in a manner consistent with the manufacturer’s specifications for the equipment. [20 DCMR 201]

f.	At all times, including periods of startup, shutdown, and malfunction, the Permittee shall, to the extent practicable, maintain and operate the boiler in a manner consistent with good air pollution control practice for minimizing emissions.  Determination of whether acceptable operating procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source. [20 DCMR 201]

IV.	Monitoring and Testing Requirements:

a.	At least once during the term of this permit, the Permittee shall conduct performance testing on the boiler using each of the fuels (natural gas and #2 fuel oil), to determine compliance with Conditions II(a) (except SO2 which can be calculated based on fuel sulfur data) and (d) and shall furnish the Department with a written report of the results of such performance test in accordance with the following requirements [20 DCMR 502]:

1.	One (1) original and one (1) copy of the test protocol shall be submitted to the following address a minimum of thirty (30) days in advance of the proposed test date.  The test shall be conducted in accordance with Federal and District requirements.

Chief, Compliance and Enforcement Branch

Air Quality Division

Department of Energy and Environment

1200 First Street NE, 5th Floor

Washington, DC 20002

2.	The test protocol shall be approved by the Department prior to initiating any testing.  Upon approval of the test protocol, the Company shall finalize the test date with the assigned inspector in the Compliance and Enforcement Branch.  The District must have the opportunity to observe the test for the results to be considered for acceptance.

3.	The final results of the testing shall be submitted to the Department within sixty (60) days of the test completion.  One (1) original and one (1) copy of the test report shall be submitted to the address in Condition IV(a) (1) above.

4.	The final report of the results shall include the emissions test report (including raw data from the test) as well as a summary of the test results and a statement of compliance or non-compliance with permit conditions to be considered valid.  The summary of results and statement of compliance or non-compliance shall contain the following information:

A.	A statement that the Permittee has reviewed the report from the emissions testing firm and agrees with the findings.

B.	Permit number(s) and condition(s) which are the basis for the compliance evaluation.

C.	Summary of results with respect to the permit condition.

D.	Statement of compliance or non-compliance with each permit condition.

5.	The results must demonstrate to the Department’s satisfaction that the emission unit is operating in compliance with the applicable regulations and conditions of this permit; if the final report of the test results shows non-compliance the Permittee shall propose corrective action(s).  Failure to demonstrate compliance through the test may result in enforcement action.

b.	The Permittee shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested.  [20 DCMR 502.1]

c.	At least once per quarter when operating on natural gas and at least once per week when operating on No. 2 fuel oil, during operation of the boiler, the Permittee shall conduct visual observations of the emissions from the boiler.  If no operations are occurring for a given boiler during a given quarter, this shall be so noted.  If emissions are visible, the Permittee shall make arrangements for prompt visible emissions testing by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A). Such a test shall consist of a minimum of 30 minutes of opacity observations for the boiler in question and shall be performed while firing the same fuel as was in use when the visible emissions were observed.

d.	Regardless of whether or not emissions are observed pursuant to Condition IV(c) of this permit, the Permittee shall conduct a minimum of one visible emissions test of the boiler each year for each fuel burned since the last visible emissions test required under this permit condition.  If the only combustion of a given fuel burned since the last test was burned during periodic testing required by this permit, no visible emission test for that fuel will be required under this condition.

1.	Such a test program shall consist of a minimum of 30 minutes of opacity observations of the boiler firing each fuel and shall be performed by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).

2.	Prior to such a test, the Permittee shall notify the Compliance and Enforcement Branch of the scheduled date of the test by one of the following methods:

A.	 The Permittee shall submit a letter via postal mail to the address in Condition IV(a)(1), postmarked at least fifteen (15) days prior to the scheduled date of the test;

B.	The Permittee shall drop off a letter at the Department's Office, addressed to the Chief of the Compliance and Enforcement Branch of the Air Quality Division at least ten (10) days prior to the scheduled date of the test; or

C.	The Permittee shall submit an email to the Chief of the Compliance and Enforcement Branch at least ten (10) days prior to the scheduled date of the test. The appropriate email address can be obtained by calling the Air Quality Division number at (202) 535-2250

e.	To show compliance with Condition III(b), the Permittee shall obtain and maintain records in accordance with Condition V(d).  Additionally, the Department reserves the right to require supplemental sampling and testing of the fuel oil to confirm the certifications provided by the fuel supplier.  If such sampling is required, it shall be performed in accordance with the following methods:

1.	To obtain fuel samples:

A.	ASTM D 270, “Standard Method of Sampling Petroleum and Petroleum Products;”

B.	ASTM D 4057, “Practice for Manual Sampling of Petroleum and Petroleum Products;” or

C.	ASTM D 4177, “Standard Practice for Automatic Sampling of Petroleum and Petroleum Products;”

2.	To determine the fuel oil grade: ASTM D 396, “Standard Specification for Fuel Oils;”

3.	To determine the sulfur concentration of fuels:

A.	ASTM D 129, “Standard Test Method for Sulfur in Petroleum Products (General Bomb Method)”;

B.	ASTM D 1266, “Standard Test Method for Sulfur in Petroleum Products (Lamp Method)”;

C.	ASTM D 1552, “Standard Test Method for Sulfur in Petroleum Products (High-Temperature Method”;

D.	ASTM D 2622, “Standard Test Method for Sulfur in Petroleum Products by Wavelength Dispersive X-Ray Fluorescence Spectrometry”;

E.	ASTM D 4294, “Test Method for Sulfur in Petroleum and Petroleum Products by Energy Dispersive X-ray Fluorescence Spectrometry;” or

F.	ASTM D 5453, “Standard Test Method for Determination of Total Sulfur in Light Hydrocarbons, Spark Ignition Engine Fuel, Diesel Engine Fuel, and Engine Oil by Ultraviolet Fluorescence;” and

4.	Other methods developed or approved by the Department or EPA.

f.	The Permittee shall monitor the operation of the boiler in a manner consistent with a good preventive maintenance program.

g.	The Permittee shall monitor the type and amount of fuel burned in the boiler, along with the reason for and duration of any use of No. 2 fuel oil.

h.	The Permittee shall monitor the total number of hours each calendar month that the boiler is operated on No. 2 fuel oil.  These shall be summed each month for the boiler and these sums shall be tracked in a rolling 12-month format to ensure compliance with Condition III(d).

i.	The Permittee shall monitor the stack outlets and identify any visible emissions to ensure that if they occur, the problem is identified and repaired.

V.	Record Keeping and Reporting Requirements:

The following information shall be recorded and maintained in a log at the facility for

a period not less than five (5) years from the date the information is obtained. [20 DCMR 302.1(c)(2)(B) and 20 DCMR 500.8]

a.	The Permittee shall keep records of the results of all emissions testing required for the

boiler pursuant to Conditions IV(a) and (b) of this permit. [20 DCMR 500.8 and 20 DCMR 201]

b.	The Permittee shall maintain records of all visible emissions monitoring performed pursuant to Condition IV(c), including notes indicating when no observations were performed as a result of not operating the boiler that quarter.  These records shall be maintained in an organized fashion, shall include the identity of the person performing the monitoring, and shall be readily available for inspection by the Deparatment. [20 DCMR 302.1(c)(2)(B) and 20 DCMR 500.8]

c.	The Permittee shall maintain records of all Method 9 visible emissions testing performed pursuant to Conditions IV(c) and (d).  These records shall also include the identity of the person performing the visible emissions testing and documentation of his/her Method 9 certification.  These records shall include documentation indicating whether the results show compliance with Condition II(b). [20 DCMR 500.8]

d.	For each delivery of No. 2 fuel oil, the Permittee shall obtain from the fuel supplier an electronic or paper record of the following fuel data (Note that a product transfer document that meets federal requirements and contains this these data, such as a Bill of Lading, may be used to meet these requirements and shall be considered a certification that the information is accurate.):

1.	The date of delivery;

2.	The name, address, and telephone number of the transferor (the fuel supplier);

3.	The name and address of the transferee (the Permittee or Permittee’s representative);

4.	The volume of fuel oil being sold or transferred;

5.	The fuel oil grade; and

6.	The sulfur content of the fuel oil as determined using the sampling and testing methods specified in Condition IV(e), which may be expressed as the maximum allowable sulfur content.

e.	The Permittee shall maintain records of all instances of boiler operation using No. 2 fuel oil, including the reason for operation using that fuel and the number of hours the boiler is operated using that fuel. [20 DCMR 500.8]

f.	The Permittee shall maintain records of the amount of each fuel used each month in the boiler. These monthly data shall, in turn, be maintained in a calendar year total sum format.  [20 DCMR 302.1(c)(2)(B), 20 DCMR 500.2 and 20 DCMR 500.8]

g.	The Permittee shall maintain records of the number of hours the boiler is operated each month on No. 2 fuel oil. These data shall be summed each month.  These resultant sums shall be maintained in a 12-month rolling sum format to determine compliance with Condition III(d).

h.	The Permittee shall keep records of all maintenance performed on the boiler so as to document compliance with Conditions III(e) and (f).  These records shall be initialed to attest to their accuracy.

i.	Based on the fuel usage records collected pursuant to this permit, the Permittee shall submit the total annual (calendar year basis) emissions from this boiler as part of the annual emissions statement submitted pursuant to the requirements of Chapter 3 (Title V) permit No. 008-R2, Condition I(d)(2)(C), and due by March 1 of each year, until such time as the requirements of this permit are included in a revised Title V permit.

j.	The Permittee shall certify compliance or non-compliance with each condition of this permit as part of (or as a supplement to) the semi-annual reports and annual compliance certification required to be submitted to the Department pursuant to Chapter 3 (Title V) permit No. 008-R2, Conditions I(d)(1) and (2), in accordance with the requirements of those conditions. [20 DCMR 302.1(c)(3) and 302.3(e)(3)]

If you have any questions, please call me at (202) 535-1747 or Olivia Achuko at (202) 535-2997.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:OA