June 25, 2019

Nicholas Carros

Sustainability Manager

United States Department of State

2201 C Street NW, B2A61

Washington DC 20520

**RE: Permits Nos. 6892-R1 through 6900-R1 to Operate Nine (9) 6.0 MMBTU/hour Natural Gas-Fired Boilers**

Dear Mr. Carros:

Pursuant to §200.1 and §200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit shall be obtained from the Department of Energy and Environment (the Department) before any person may cause or allow the construction or operation of a stationary source in the District of Columbia. The applications of the United States Department of State (the Permittee) to operate the following nine (9) 6.0 MMBTU/hr natural gas-fired boilers at 2201 C Street NW, Washington DC 20520, have been reviewed:

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Permit No.** | **Equipment Size (MMBTU/hr)**  | **Manufacturer** | **Unit Number** | **Serial Number** |
| 6892-R1 | 6.0 | Fulton | Boiler 1 | 8454 |
| 6893-R1 | 6.0 | Fulton | Boiler 2 | 8455 |
| 6894-R1 | 6.0 | Fulton | Boiler 3 | 8441 |
| 6895-R1 | 6.0 | Fulton | Boiler 4 | 8456 |
| 6896-R1 | 6.0 | Fulton | Boiler 5 | 8440 |
| 6897-R1 | 6.0 | Fulton | Boiler 6 | 8439 |
| 6898-R1 | 6.0 | Fulton | Boiler 7 | 8566 |
| 6899-R1 | 6.0 | Fulton | Boiler 8 | 8567 |
| 6900-R1 | 6.0 | Fulton | Boiler 9 | 8565 |

Based on the submitted plans and specifications as detailed in the applications received on March 5, 2019, the operation of the boilers is permitted, subject to the following conditions:

I. General Requirements:

* 1. This approval is issued pursuant to the applicable air pollution control requirements of 20 DCMR for the construction and operation of the boilers.

b. This set of permits will expire on June 24, 2024. If continued operation after this date is desired, the owner or operator shall submit application for renewal by March 24, 2024. [20 DCMR 200.4]

c. Construction or operation of equipment under the authority of this set of permits shall be considered acceptance of its terms and conditions.

1. The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1. Enter upon the Permittee’s premises where a source or emission units are located, an emissions related activity is conducted, or where records required by this permit are kept;

2. Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3. Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4. Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

1. This set of permits shall be kept on the premises and produced upon request.
2. Failure to comply with the provisions of this permit may be grounds for suspension or revocation. [20 DCMR 202.2]

**II. Emission Limitations:**

* 1. Emissions of criteria pollutants from each of the nine (9) boilers shall not exceed those specified in the following table [20 DCMR 201]:

|  |
| --- |
| **Boiler Emission Limits** |
| **Pollutant** | **Short-Term Limit (lb/hr)** |
| Carbon Monoxide (CO) | 0.494 |
| Oxides of Nitrogen (NOx) | 0.216 |
| Total Particulate Matter (PM Total)\* | 0.0447 |
| Sulfur Dioxide (SO2) | 0.00353 |

\*PM Total includes both filterable and condensable fractions.

*Note that, unless other credible evidence of a violation is identified, such as by testing required in accordance with Condition IV(a), the Permittee will be considered to be in compliance with Condition II(a) as long as compliance is maintained with Condition III(a) of this permit.*

* 1. b. Visible emissions shall not be emitted into the outdoor atmosphere from the boiler, except that discharges not exceeding forty percent (40%) opacity (unaveraged) shall be permitted for two (2) minutes in any sixty (60) minute period and for an aggregate of twelve (12) minutes in any twenty-four hour (24 hr.) period during start-up, cleaning, adjustment of combustion controls, or malfunction of the equipment [20 DCMR 606.1]
	2. *Note that 20 DCMR 606 is subject to an EPA-issued call for a State Implementation Plan (SIP) revision (known as a “SIP call”) requiring the District to revise 20 DCMR 606. See “State Implementation Plans: Response to Petition for Rulemaking; Restatement and Update of EPA’s SSM Policy Applicable to SIPs; Findings of Substantial Inadequacy; and SIP Calls To Amend Provisions Applying to Excess Emissions During Periods of Startup, Shutdown and Malfunction”, 80 Fed. Reg. 33840 (June 12, 2015). It is likely that this federal action will result in changes to the requirements of 20 DCMR 606. Any such changes, once finalized in the DCMR, will supersede the language of Condition II(b) as stated above.*

c. An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1]

d. Particulate matter (PM) emissions from each of the nine (9) boilers shall not exceed 0.11 pound per million BTU. [20 DCMR 600.1] *Note that, unless other credible evidence of a violation is identified, such as by testing required in accordance with Condition IV(a), the Permittee will be considered to be in compliance with Condition II(d) as long as compliance is maintained with Condition III(a) of this permit.*

e. NOx and CO emissions shall not exceed those achieved with the performance of annual combustion adjustments on each boiler. To show compliance with this condition, the Permittee shall, each calendar year, perform adjustments of the combustion processes of the boilers with the following characteristics [20 DCMR 805.1(a)(4) and 20 DCMR 805.8(a) and (b)]:

i. Inspection, adjustment, cleaning or replacement of fuel burning equipment, including the burners and moving parts necessary for proper operation as specified by the manufacturer;

ii. Inspection of the flame pattern or characteristics and adjustments necessary to minimize total emissions of NOx and, to the extent practicable, minimize emissions of CO;

iii. Inspection of the air-to-fuel ratio control system and adjustments necessary to ensure proper calibration and operation as specified by the manufacturer; and

iv. Adjustments shall be made such that the maximum emission rate for any contaminant does not exceed the maximum allowable emission rate as set forth in Condition II of this permit.

**III. Operational Limitations:**

* 1. a. The only fuel permitted for the boilers shall be natural gas. No other fuels are approved for use. [20 DCMR 201]
	2. b. This approval is valid for the specific activity cited in the application submitted to this office. Any deviation from the specific activity is a violation of the permit.

c. The boilers shall be operated at all times in a manner consistent with the manufacturer’s specifications for the equipment. [20 DCMR 201]

d. At all times, including periods of startup, shutdown, and malfunction, the owner or operator shall, to the extent practicable, maintain and operate each boiler in a manner consistent with good air pollution control practice for minimizing emissions. Determination of whether acceptable operating procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source. [20 DCMR 201]

**IV. Monitoring and Testing Requirements:**

a. The Permittee shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested. [20 DCMR 502.1]

b. If the Department requests testing pursuant to Condition IV(a) of this permit, the Permittee shall conduct performance testing on the boiler using natural gas, to determine compliance with Conditions II(a) (except SO2) and (d) and shall furnish the Department with a written report of the results of such performance test in accordance with the following requirements [20 DCMR 502]:

1. One (1) original test protocol shall be submitted to the following address a minimum of thirty (30) days in advance of the proposed test date. The test shall be conducted in accordance with Federal and District requirements.

Chief, Compliance and Enforcement Branch

Air Quality Division

1200 First Street NE

5th Floor

Washington, DC 20002

2. The test protocol and test date(s) shall be approved by the Department prior to initiating any testing. The Department must have the opportunity to observe the test for the results to be considered for acceptance.

3. The final results of the testing shall be submitted to the Department within sixty (60) days of the test completion. One (1) original copy of the test report shall be submitted to the address in Condition IV(b)(1) above.

4. The final report of the results shall include the emissions test report (including raw data from the test) as well as a summary of the test results and a statement of compliance or non-compliance with permit conditions to be considered valid. The summary of results and statement of compliance or non-compliance shall contain the following information:

A. A statement that the owner or operator has reviewed the report from the emissions testing firm and agrees with the findings.

B. Permit number(s) and condition(s) which are the basis for the compliance evaluation.

C. Summary of results with respect to the permit condition.

D. Statement of compliance or non-compliance with each permit conditions.

5. The results must demonstrate to the Department’s satisfaction that the emission unit is operating in compliance with the applicable regulations and conditions of this permit; if the final report of the test results shows non-compliance the owner or operator shall propose corrective action(s). Failure to demonstrate compliance through the test may result in enforcement action.

c. At least once per quarter, during operation of each boiler, the Permittee shall conduct visual observations of the emissions from each boiler. If no operations are occurring for a given boiler during a given quarter, this shall be so noted. If emissions are visible, the Permittee shall make arrangements for prompt visible emissions testing by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A). Such a test shall consist of a minimum of 30 minutes of opacity observations for the boiler in question and shall be performed while firing the same fuel as was in use when the visible emissions were observed.

d. Regardless of whether or not emissions are observed pursuant to Condition IV(c) of this permit, the Permittee shall conduct a minimum of one visible emissions test of each boiler each year for each fuel burned that year. Such a test program shall consist of a minimum of 30 minutes of opacity observations of each boiler firing each fuel and shall be performed by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).

**V. Record Keeping and Reporting Requirements:**

The Permittee shall maintain the following records for a period of not less than five (5) years from the date of each test, monitoring, sample measurement, report, application, or other activity: [20 DCMR 302.1(c)(2)(B) and 20 DCMR 500.2 and 500.8]

a. The Permittee shall keep records of the results of all emissions testing required for the boiler pursuant to Conditions IV(a) and (b) of this permit. [20 DCMR 201 and 20 DCMR 500.8]

b. The Permittee shall maintain records of all visible emissions monitoring performed pursuant to Condition IV(c), including notes indicating when no observations were performed as a result of not operating of the boiler that quarter. These records shall be maintained in an organized fashion, shall include the identity of the person performing the monitoring, and shall be readily available for inspection by the Department. [20 DCMR 500.8]

c. The Permittee shall maintain records of all Method 9 visible emissions testing performed pursuant to Conditions IV(c) and (d). These records shall also include the identity of the person performing the visible emissions testing and documentation of his/her Method 9 certification. These records shall include documentation indicating whether the results show compliance with Condition II(b). [20 DCMR 500.8]

d. The Permittee shall maintain records of the amount of fuel used each month in the boiler. These data shall be totalized for each calendar year.

e. The Permittee shall keep records of the following information regarding the combustion adjustments required pursuant to Condition II(e): [20 DCMR 805.8(c)]

1. The date on which the combustion process was last adjusted;

2. The name, title, and affiliation of the person who made the adjustments;

3. The NOx emission rate, in ppmvd, after the adjustments were made;

4. The CO emission rate, in ppmvd, after the adjustments were made;

5. The CO2 concentration, in percent (%) by volume dry basis, after the adjustments were made;

6. The O2 concentration, in percent (%) by volume dry basis, after the adjustments were made; and

7. Any other information that the Department may require.

If you have any questions, please call me at (202) 535-1747 or Abraham Hagos at (202) 535-1354.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:ATH