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May 5, 2026
	
Raoul Fernandez, Project Manager
CBNA Halmar Clean Rivers JV
1441 L Street NW, Suite 610
Washington, DC 20005

RE:	Permit No. 7421 to Construct and Operate One (1) 430 kWe Diesel-Fired Non-Emergency Generator Set at West Potomac Park, 1601 Ohio Drive SW, Washington, DC

Dear Raoul Fernandez:	

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit from the Department of Energy and Environment (the Department) shall be obtained before any person can construct and operate a stationary source in the District of Columbia. The application of CBNA Halmar Clean Rivers JV  (the Permittee) to construct and operate a 430 kWe Stamford diesel-fired non-emergency generator set, model HCl534C1 with S/N N21J400288 and driven by a 515 kWm (700 bhp) Volvo engine with serial number 2016151373 (TAD1670-1672VE) at the West Potomac Park site, 1601 Ohio Drive SW Washington, DC, per the submitted plans and specifications received on June 18, 2025, as revised by submittals on July 28, 2025, July 31, 2025, and August 11, 2025, is hereby approved, subject to the following conditions:

I.	General Requirements:

a.	The emergency generator shall be installed, maintained, and operated in accordance with the applicable sections of Title 20 of the District of Columbia Municipal Regulations (20 DCMR).

b.	This permit will expire on May 4, 2031 [20 DCMR 200.4].  If continued operation after this date is desired, the Permittee shall submit an application for renewal by January 4, 2031.

c.	Construction or operation of equipment under the authority of this permit shall be considered acceptance of its terms and conditions.

d.	The Permittee shall allow authorized officials of the District, upon presentation of identification, to: 

1.	Enter upon the Permittee’s premises where a source or emission unit is located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit; 

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

e.	This permit shall be kept on the premises and produced upon request.

f. Failure to comply with the provisions of this permit may be grounds for suspension or revocation. [20 DCMR 202.2]

II.	Emission Limitations:

[bookmark: _Hlk218511920]a.	Emissions from this generator shall not exceed those in the following table as tested pursuant to the applicable test methods in 40 CFR 1039, Subpart F [40 CFR 60.4200(a)(1)(i), 40 CFR 60.4200(a)(2)(i), 40 CFR 60.4201(a), 40 CFR 60.4204(b), 40 CFR 1039.101(a), (b), (d), and (e)]:

	
	Pollutant Emission Limits (g/kW-hr)

	Emission Standard Type
	NOx
	CO
	NMHC
	PM 

	Transient and Steady State
	0.40
	3.5
	0.19
	0.03†

	Not-to-Exceed
	0.60
	4.4
	0.29
	0.05


†	A family emission limit (FEL) has been granted by the U.S. Environmental Protection Agency (EPA) for this unit pursuant to 40 CFR 1039.101(d) as noted on the Certificate of Conformity for this engine.

[bookmark: _Hlk218512047]b.	Visible emissions shall not be emitted into the outdoor atmosphere from the engine, except that discharges shall be permitted for two (2) minutes during any start-up, cleaning, adjustment of combustion or operational controls, or regeneration of emissions control equipment; provided, that such discharges shall not exceed twenty-seven percent (27%) opacity (unaveraged). [20 DCMR 606.1 and 606.2(d)]

c.	An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1] 

Violation of the requirements of this condition that occur as a result of unavoidable malfunction, despite the conscientious employment of control practices, shall be an affirmative defense for which the owner or operator shall bear the burden of proof. A malfunction shall not be considered unavoidable if the owner or operator could have taken, but did not take, appropriate steps to eliminate the malfunction within a reasonable time, as determined by the Department. [20 DCMR 903.13(b)]

This condition is District enforceable only.

d.	The Permittee shall comply with the requirements for crankcase emissions, adjustable parameters, prohibited controls, and defeat devices specified in 40 CFR 1039.115. [40 CFR 60.4201(a), 40 CFR 60.4204(b)]

III.	Operational Limitations:

a.	The generator engine shall fire only diesel fuel that contains a maximum sulfur content of 15 ppm (0.0015 percent by weight) and either a minimum cetane index of 40 or a maximum aromatic content of 35 volume percent. [20 DCMR 801.1, 40 CFR 60.4207(b), and 40 CFR 1090.305] Note that this is a streamlined requirement. Compliance with the more stringent requirement of 40 CFR 60.4207(b) reflected here will ensure compliance with 20 DCMR 801.1.

b.	The generator shall not be operated in conjunction with a voluntary demand-reduction program or any other interruptible power supply arrangement with a utility, other market participant, or system operator. [20 DCMR 201]

c.	The generator set and all components shall be maintained and operated as follows: [40 CFR 60.4211(a) and (c), 20 DCMR 606.4(b), and 20 DCMR 201]

1.	Install, configure, operate and maintain the stationary CI internal combustion engine and control device according to the manufacturer's emission-related written instructions;

2.	Change only those emission-related settings that are permitted by the manufacturer; and

 3. Meet the requirements of 40 CFR part 1068, as they apply to this generator set.

d. At all times, including periods of startup, shutdown, and malfunction, the Permittee shall, to the extent practicable, maintain and operate the engine in a manner consistent with good air pollution control practice for minimizing emissions. Determination of whether acceptable operating procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source. [20 DCMR 201, 20 DCMR 606.4(a)]

e. [bookmark: _Hlk152168415]The Permittee shall ensure that persons participating in the maintenance and operation of the equipment are adequately trained and supervised to meet the requirements of Conditions III(c) and (d). [20 DCMR 606.4(c)]

IV.	Monitoring and Testing Requirements:

a.	The Permittee shall monitor the total number of hours of operation of the generator set each month with the use of a properly operating non-resettable hour meter installed on the unit. [20 DCMR 500.1, 40 CFR 60.4209(a) and 40 CFR 60.4214(b)]

b.	The Permittee shall monitor and/or test the sulfur content in the diesel fuel obtained for use in the generator engine as necessary to show compliance with Conditions III(a) and V(c) in accordance with appropriate ASTM methods. [20 DCMR 502.3 and 502.6]

c.	The Permittee shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested.  [20 DCMR 502.1]

d.	The Permittee shall maintain an awareness of the operation of the generator set to identify potential exceedances of Conditions II(b) and (c). If significant visible emissions are observed from the unit, the Permittee shall have the visible emissions tested by a qualified person certified to perform testing pursuant to 40 CFR 60, Reference Method 9. [20 DCMR 502.1]

e.	The Permittee shall investigate the cause of any malfunction of the equipment. [20 DCMR 606.5(b)]

V.	Record Keeping and Reporting Requirements:

a.	Except where a longer period is specified herein, the Permittee shall maintain all records necessary for determining compliance with this permit in a readily accessible location at the facility, or an electronic location readily accessible from the facility, for a minimum of three (3) years from the date each record is recorded and shall make these records available to the Department and EPA upon written or verbal request. [20 DCMR 104.2(b), 20 DCMR 500.8, and 20 DCMR 606.5(d)] All records shall be maintained in such a manner that authorized representatives can certify their accuracy under penalty of D.C. Official Code § 8-101.05e pertaining to false statements, and have either done so in the records, or will do so upon request at the time they are made available to the Department or EPA. [20 DCMR 104.2 and 20 DCMR 500.8] The following records shall be maintained:	

1.	The total hours of operation for each month and the cumulative 12-month rolling period shall be calculated and recorded within 15 days of the end of each calendar month for the previous month and the 12-month period ending at the end of that month;

2.	Records of the maintenance performed on the unit, sufficient to show compliance with Conditions III(c) and (d);

3. Records of the results of any visible emissions monitoring performed; 

4. Records of any complaints received by the Permittee about the operation of the generator set;

5. Records of the occurrence and duration of each malfunction of operation; 

6. Records of the actions taken during periods of malfunction to minimize emissions, including corrective actions to restore malfunction process and air pollution control and monitoring equipment to its normal or usual manner of operation;

7.	Records of the date, time, and duration of any equipment manual startup, manual shutdown, cleaning, emission control regeneration, and malfunction [20 DCMR 606.5(a)]; 

8.	Records of the investigatory activities and conclusions of any investigation of any malfunction of the equipment pursuant to Condition IV(e); and

9.	Records of the training performed to comply with Condition III(e).

b.	The Permittee shall maintain a copy of the generator’s manufacturer’s maintenance and operating recommendations at the facility. [20 DCMR 501]

c.	For each delivery of diesel fuel, the Permittee shall maintain one of the following:

1.	A fuel delivery receipt containing the date, fuel type, and amount of the delivery and certification from the fuel supplier that the fuel delivered was tested in accordance with an appropriate ASTM method (specified in the certification) and met the requirements of Condition III(a); or

2.	A fuel delivery receipt and documentation of sampling and analysis containing the following information:

A.	The fuel oil type and the ASTM method used to determine the type (see the definition of distillate oil in 40 CFR 60.41c for appropriate ASTM methods);

B.	The weight percent sulfur of the fuel as determined using ASTM test method D-4294 or D-5453 or other methods approved in advance by the Department;

C.	The date and time the sample was taken;

D.	The name, address, and telephone number of the laboratory that analyzed the sample; and

E.	The test method used to determine the sulfur content.

    d.	The Permittee shall maintain a copy of the EPA Certificate of Conformity at the facility at all times. [20 DCMR 500.1]

    e.    The Permittee shall, within ten (10) days of becoming aware of a violation of any             condition of this permit, submit a written report to the Department at the following address [20 DCMR 502]:

air.quality@dc.gov 

If you have any questions, please contact me at (202) 498-8143 or stephen.ours@dc.gov or John Nwoke at (202) 724-7778 or john.nwoke@dc.gov.

Sincerely,



Stephen S. Ours, P.E.
Chief, Permitting Branch

SSO:JCN
[image: ][image: ]1200 First Street NE, 5th Floor, Washington, DC 20002 | (202) 535-2600 | doee.dc.gov 

image1.jpeg
=

*W




image2.jpeg
DEPARTMENT
OF




